## Sheet1
fu_roomNumber | New Building Code | ActionRequested | fu_description | fu_unitID | wo_number | wo_requestDate | TechComments
204-LS2 | FNA | Gravitometer not working @ Fauna incoming 12". | 12" Houston(EPL) to Fauna | 1-204-LS2 | HU-16081 | 2009-09-29 01:28 | repaired Solatron converter power supply
205-LS1 | FNA | Fauna and Wynnewood gravitometers do not match. A little over 1 degree. ... EMT Called Out: NONE ... throughput_loss: No | 12" Fauna to Wynnewood | 1-205-LS1 | HU-20111 | 2013-11-22 15:02 | One gravitometer is an ultrasonic meter. The gravity is not as accurate as a solartron or an insertion type. It is only for reference.
211-LS1 | NHO | N Houston station, Comm loss. took it offscan. | 10" N Houston Line to Plantersville | 1-211-LS1 | HU-17629 | 2010-10-13 05:10 | During installation of new comms system, breaker was tripped, reset breaker.
222-LS | PTA | out station sph indicater did not work | 28" Port Arthur Station to Houston | 1-222-LS | HU-14278 | 2008-06-14 10:13 | phone line issue ongoing
222-LS | PTA | preview sphere detector, there was no indication | 28" Port Arthur Station to Houston | 1-222-LS | HU-15869 | 2009-08-26 16:09 | Received indication that the sphere hit outstation on Houston station HMI. Spoke with Sam Sansone, and he found that the indication was on the alarm history at the CCT's console. No malfunction found.
222-LS | PTA | Outstation pig sig did not work | 28" Port Arthur Station to Houston | 1-222-LS | HU-17086 | 2010-06-22 02:37 | Sphere detection worked as it was supposed to and was acknowledged by the CCT.
222-LS | PTA | sphere didn't show hitting outstation | 28" Port Arthur Station to Houston | 1-222-LS | HU-17627 | 2010-10-12 07:31 | Replaced pig sig.
222-LS | PTA | No sphere indication on outstation (PTA) | 28" Port Arthur Station to Houston | 1-222-LS | HU-17630 | 2010-10-13 11:41 | Replaced pig sig.
222-LS | PTA_HAN_ROBV008.98 | ROBV-8.98 showing fault on valve control. | 28" Port Arthur Station to Houston | 1-222-LS | HU-17906 | 2010-08-16 18:58 | Alan Frazier spoke with Doug Ashby, and Doug is looking into a solution. Doug assured Alan that there was nothing that Alan could do to resolve the problem.
223-LS | HOU | Pasadena outstation gravity pmp seal leaking, float switch did not activate alarm in seal pot. | 28" Line Pasadena-Houston | 1-223-LS | HU-13393 | 2007-07-26 21:19 | Omar performed the repair, I closed on this date 10/18/07
223-LS | HOU | Surge system alarm is going off intermittently. Surge system has relieved 3 times and the system has worked but we continue to get alarms without legitimate surges on FS402. | 28" Line Pasadena-Houston | 1-223-LS | HU-13582 | 2007-11-22 11:55 | replaced oring on PRV-102, had cuts, and smashed .
223-LS | HOU | Houston outstation gravitometer from pasadena is not working. hasn't changed gravity since 10/11/08. | 28" Line Pasadena-Houston | 1-223-LS | HU-14842 | 2008-11-19 14:06 | FOUND UPS SYSTEM IN FAULT, RESET POWER AND TESTED OK, GRAVITY SIGNAL UPDATING OK
223-LS | HOU | 28 inch Wallisville out station gravitometer seal fail EMT Called Out: Derek Freisner | 28" Line Pasadena-Houston | 1-223-LS | HU-17195 | 2010-08-10 13:00 | Seal failed on pump. Replaced seal and put pump back in service.
223-LS | HOU | No sphere indication on outstation. | 28" Line Pasadena-Houston | 1-223-LS | HU-17494 | 2010-10-13 11:41 | Breaker tripped at outstation causing COMM loss.
223-LS | HOU | Out station gravitometer not updating | 28" Line Pasadena-Houston | 1-223-LS | HU-17495 | 2010-10-13 11:40 | Breaker tripped at outstation causing COMM loss
223-LS | HOU | Out sta. sph indicator did not work. Gravity worked fine. Just no sph. indication. | 28" Line Pasadena-Houston | 1-223-LS | HU-17904 | 2010-11-16 06:52 | Replaced pig sig
224-LS | HOU | Prover not working | 12" line Houston Sta to Galena Park | 1-224-LS | HU-13589 | 2007-12-25 10:31 | After testing found all limit switches in working order. Verified the operation and setting of the differential switch. Prover was ran in manual for a trial six times. I then had CCT run a formal with no issues. Deviation was .028%
224-LS | HOU | 21:50-Delivery tic.CHV-75-061-PTA Seq #2500 for 35057 bbls. did not show up in completed tic. window. | 12" line Houston Sta to Galena Park | 1-224-LS | HU-14138 | 2008-02-22 04:12 | replaced pickup coil
225-LS | HOU | ESD lock out pumps | 28" line Houston Sta to Palestine | 1-225-LS | HU-13177 | 2007-07-20 09:14 | Worked with Gilbert and Tim Walker and found it was a diferential across the strainer along with the new lower pressure settings which caused this.
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4 block valve locked out. No comms | 28" line Houston Sta to Palestine | 1-225-LS | HU-14271 | 2008-05-15 18:30 | replaced the battery charger and no further issues at this site
225-LS | HOU_CON_ROBV077.39 | comm.out at ROBV 77.4 | 28" line Houston Sta to Palestine | 1-225-LS | HU-14486 | 2008-06-21 14:55 | out of service per Sam Sansone
225-LS | HOU_CON_ROBV077.39 | mpt.77.4 loss comm. | 28" line Houston Sta to Palestine | 1-225-LS | HU-14490 | 2008-07-08 16:13 | Out of service per Sam Sansone
225-LS | HOU_CON_ROBV077.39 | Loss comm. at m.p.77.4 | 28" line Houston Sta to Palestine | 1-225-LS | HU-14491 | 2008-07-09 19:45 | out of service per Sam Sansone
225-LS | CON | Conroe Pump #2 will not start ATL. Technicians have been working on motor. Started ATL and station dropped out. Will re-test at a later time. VFD currently working. Malfunction request per Steve Tollette | 28" line Houston Sta to Palestine | 1-225-LS | HU-14715 | 2008-05-21 14:52 | VFD in working condition--system test --ok
225-LS | HOU_CON_ROBV077.39 | Recieving fault alarm on Block valve 77.4 | 28" line Houston Sta to Palestine | 1-225-LS | HU-15512 | 2009-05-11 21:31 | 77.4 alarm was old and on refresh went away.
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 loss of Communication | 28" line Houston Sta to Palestine | 1-225-LS | HU-15778 | 2009-07-07 12:48 | ROBV 159.2 equipment was removed from the site in order to excavated contaminated soil. The ROBV equipment is scheduled to be re-installed starting the week of July 20, 2009.
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 is in alarm condition, and is showing error on robv overview page | 28" line Houston Sta to Palestine | 1-225-LS | HU-15968 | 2009-09-20 19:26 | Valve was tanken out of service and placed on the equipment out-of-service list on Thursday 9/17/09 due to ground settle. The ground settle caused the valve operator conduits to pull loose from the valve operator. Hand excavation of the conduits and repair is scheduled for 9/22/09.
225-LS | PAL | unit #3 locked out--station is isolated and tagged out | 28" line Houston Sta to Palestine | 1-225-LS | GV-20846 | 2010-01-29 12:37 | For the second time, there is no malfunction. The unit is locked out for maintenance.
225-LS | HOU_CON_ROBV097.17 | ROBV MP 97.2 Maint. Alert, AC Voltage Fail, Valve control. went into FAULT. Called EMT and he is checking on it. | 28" line Houston Sta to Palestine | 1-225-LS | HU-17087 | 2010-06-28 00:42 | Utility power was down for 3 hours. After resored the alarms cleared.
225-LS | HOU_CON_ROBV077.39 | ROBV MP 77.4 comm keep going off and coming back on. | 28" line Houston Sta to Palestine | 1-225-LS | HU-17088 | 2010-06-27 04:41 | Problem was resolved in Contol Center per Aaron Mosier.
225-LS | HOU_CON_ROBV097.17 | I closed ROBV 92.7 and it is showing closed but the % is 95% closed | 28" line Houston Sta to Palestine | 1-225-LS | HU-17229 | 2010-03-25 16:05 | worked with Sam and adjusted the pot to show the best resolution possible.
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4 comm keeps going in and out. | 28" line Houston Sta to Palestine | 1-225-LS | HU-17353 | 2010-09-04 20:23 | weather related
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 has Maint. Alert, and AC Voltage Fail EMT Called Out: David Emfinger | 28" line Houston Sta to Palestine | 1-225-LS | HU-17358 | 2010-09-10 14:25 | power outage--power was restored 35 minutes later--valve ok
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4 comm has been going in and out. | 28" line Houston Sta to Palestine | 1-225-LS | HU-17365 | 2010-09-22 18:50 | block valve OK on arrival bad weather in area
225-LS | PTA_HAN_ROBV008.98 | ROBV-8.98 sends AC Voltage Fail and Valve Control alarms, then clears, then sends again, then clears etc... | 28" line Houston Sta to Palestine | 1-225-LS | HU-17908 | 2010-12-09 03:33 | Alan Frazier spoke with Doug Ashby, and Doug is looking into a solution. Doug assured Alan that there was nothing that Alan could do to resolve the problem.
225-LS | HOU_CON_ROBV077.39 | ROBV MP 77.4 comm loss in and out all night. | 28" line Houston Sta to Palestine | 1-225-LS | HU-18303 | 2011-04-02 10:29 | Storms and Cool front passed through over weekend, and cloud cover was abundant. Spoke with Trudy Baily in the Central Control Center, and communications have been restored.
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4 com fail | 28" line Houston Sta to Palestine | 1-225-LS | HU-18330 | 2011-05-02 13:24 | Hugh's Networking replaced the DW 7700 box. Coms back up and working
225-LS | HUN_GRA_ROBV159.16 | Block valve at MP 159.2 is showing AC voltage fail and valve control went to fault. | 28" line Houston Sta to Palestine | 1-225-LS | HU-18462 | 2011-08-25 14:58 | Power fail from power company. Called in and reported the outage, and power was returned by 11:08, same day as outage.
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2, Maint, Alert - Valve Control - AC Voltage Fail. | 28" line Houston Sta to Palestine | 1-225-LS | HU-18554 | 2011-10-18 09:29 | Utility company power failure. Power was restored to the valve before responding.
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2, lost comm and it stayed in "Fault". Called CK and he stated that there were possible storms in the area. EMT Called Out: CK Nimitz | 28" line Houston Sta to Palestine | 1-225-LS | HU-18723 | 2012-01-25 16:17 | Electric Utility lost power to ROBV 159.2. Power restored at approximately 11:30. All alarms cleared. CK Nimitz 1/25/2012
225-LS | HOU_CON_ROBV097.17 | Loss of comm's at the Block Valve at M.P. 97.2. EMT Called Out: Omar Garcia | 28" line Houston Sta to Palestine | 1-225-LS | HU-18775 | 2012-02-27 17:28 | manual reset on junction box and power came up with normal comms.
225-LS | HOU_CON_ROBV097.17 | Comm Fail on ROBV 97.2 | 28" line Houston Sta to Palestine | 1-225-LS | HU-18825 | 2012-03-27 11:21 | Replaced Scadapak
225-LS | HOU_CON_ROBV077.39 | ROBV-77.4 in "Seal Fail" status. Alton Ryals notified. EMT Called Out: Alton Ryals | 28" line Houston Sta to Palestine | 1-225-LS | HU-18896 | 2012-04-23 00:44 | Wire shorted to ground causing breaker to trip
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4, communication is going out and then coming back on. | 28" line Houston Sta to Palestine | 1-225-LS | HU-18899 | 2012-04-08 08:18 | Storms in the area affecting satellite communications
225-LS | HUN_GRA_ROBV159.16 | ROBV-159.2 valve control showing fault. | 28" line Houston Sta to Palestine | 1-225-LS | HU-18949 | 2012-05-12 07:18 | power outage--came back in working order
225-LS | HUN_GRA_ROBV159.16 | AC Voltage fail,Maint. Alert, ... Valve Control alarms @ ROBV 159.2 EMT Called Out: David Emfinger | 28" line Houston Sta to Palestine | 1-225-LS | HU-18950 | 2012-05-12 12:50 | power outage--came back in working order
225-LS | HUN_GRA_ROBV159.16 | Fault on valve control. ... ROBV 159.2, Valve Control, Maint. Alert, AC Voltage Fail EMT Called Out: David Emfinger | 28" line Houston Sta to Palestine | 1-225-LS | HU-18994 | 2012-06-03 01:18 | power outage--came back after two hours
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2, AC Voltage fail EMT Called Out: CK Nimitz | 28" line Houston Sta to Palestine | 1-225-LS | HU-19006 | 2012-06-13 10:55 | Power fail. Restored by Houston County Electic Co-op
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 LOSS OF COMMUNICATIONS EMT Called Out: CK Nimitz | 28" line Houston Sta to Palestine | 1-225-LS | HU-19123 | 2012-08-11 01:23 | Pending - I checked the site on Friday night, 8/10/12. Tried the local reset and all systems appeared to be normal, but the CCT could not remotely see the valve. Doug Ashby put in a trouble ticket for repair with Hughes Net satellite repair. Awaiting scheduled repair date. CK Nimitz 8/13/12 Hughes Net technecian replaced the "radio" on the antenna, and the receiver power supply. He said the damage could have come from a nearby lightening strike. CK Nimitz 8/15/12
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4, communications are going in and out. | 28" line Houston Sta to Palestine | 1-225-LS | HU-19194 | 2012-09-04 11:27 | Comms have been restored
225-LS | HOU_CON_ROBV087.88 | ROBV 87.9. Communcations keeps going in and out. | 28" line Houston Sta to Palestine | 1-225-LS | HU-19200 | 2012-09-23 03:43 | Comms have been restored
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 Maint. Alert AC Voltage Fail EMT Called Out: CK Nimitz | 28" line Houston Sta to Palestine | 1-225-LS | HU-19382 | 2012-12-25 13:59 | Loss of incoming power on 12/25/2012 during storms. Power restored by power company on 12/27/2012. CK Nimitz 12/27/2012
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4 87.9 going in and out of comm | 28" line Houston Sta to Palestine | 1-225-LS | HU-19434 | 2013-01-20 11:39 | Exceptionaly heavy fog in the area causing problems with the satellite signal
225-LS | HOU_CON_ROBV097.17 | Loss of communication with the block valve at MP 97.2 EMT Called Out: Alton Ryals | 28" line Houston Sta to Palestine | 1-225-LS | HU-19435 | 2013-01-24 13:31 | Blown DC fuse in the SCADA PAK
225-LS | HOU_CON_ROBV087.88 | ROBV 87.9 comm loss and lockout. ... Maint alert ... DC voltage Low ... AC voltage Fail ... Valve control EMT Called Out: Omar Garcia | 28" line Houston Sta to Palestine | 1-225-LS | HU-19485 | 2013-02-09 20:16 | ARRIVED AT BLOCK VLV AND FOUND POWER POLE ON FIRE, CALLED FIRE DEPT AND POWER COMPANY , POWER COMPANY REPAIRED POLE AND GOT SERICE BACK , RESET BLOCK VLV COMMUNICATIONS AND TESTED OK.
225-LS | HOU_CON_ROBV097.17 | ROBV 97.2 ... Intermitent comm loss and Battery voltage high EMT Called Out: Omar Garcia | 28" line Houston Sta to Palestine | 1-225-LS | HU-19494 | 2013-02-09 20:15 | Replace battery charger rectifier and batteries
225-LS | HOU_CON_ROBV077.39 | ROBV 77.4 comm loss going on and off scan every few minutes | 28" line Houston Sta to Palestine | 1-225-LS | HU-19552 | 2013-03-23 11:08 | High winds and storms in the area at the time.
225-LS | HOU_CON_ROBV077.39 | ROBV 77.1 comm loss is intermitent. | 28" line Houston Sta to Palestine | 1-225-LS | HU-19626 | 2013-04-13 08:07 | Checked power, performed Local Reset and ensured CCT had comm's.
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 AC voltage fail, Maint alert and Valve control alarms ... EMT Called Out: CK Nimitz | 28" line Houston Sta to Palestine | 1-225-LS | HU-19892 | 2013-08-12 15:24 | Power came back on from utility. No action necessary. ... ... PASSED. CK Nimitz
225-LS | HUN_GRA_ROBV159.16 | ROBV 159.2 AC Voltage Fail ... EMT Called Out: CK Nimitz | 28" line Houston Sta to Palestine | 1-225-LS | HU-19900 | 2013-08-25 01:54 | Callout for loss of power to ROBV. HCEC said their trends showed that they did not lose power on that line. Went to site but power was on. Tightened all power connections inside the ROBV control panel back to the incoming power pole breaker. ... ... Passed - CK Nimmitz
225-LS | HUN_GRA_ROBV159.16 | No comm. at ROBV-159.2 ... EMT Called Out: CK Nimitz ... throughput_loss: No | 28" line Houston Sta to Palestine | 1-225-LS | HU-20057 | 2013-11-01 19:36 | Total comms loss to ROBV 159.16. Checked all incoming power and rebooted Hughes 7700. This cleared the comms issue. ... ... PASSED CK Nimitz, 11/1/2013
226-LS | GVL | Repair solenoid for 300 bbl suction valve | 28" line Greenville Sta to OK line | 2-226-LS | GV-19131 | 2009-01-05 14:00 | Replaced solenoid and verified operation.
226-LS | GVL | water leak at discharge side of Feed pump | 28" line Greenville Sta to OK line | 2-226-LS | GV-19132 | 2009-01-05 14:33 | Incorrect request
226-LS | BON_DUR_ROBV362.25 | Maint. alert, fault. ROBV 362.2 | 28" line Greenville Sta to OK line | 2-226-LS | GV-20205 | 2009-09-15 06:40 | Power outage caused the alarm. when the power came back up alarm went away.
226-LS | BON_DUR_ROBV362.25 | Comm loss at ROBV 362.2, called EMT. Possible weather related. | 28" line Greenville Sta to OK line | 2-226-LS | GV-20849 | 2010-02-11 18:09 | Malfunction weather related,snowstorm in area,when storm cleared. Comms were restore.appp 1045 on 2-12-10.
226-LS | HOL_OKM_ROBV493.10 | ROBV 493.2 CONNECT TIMEOUT | 28" line Greenville Sta to OK line | 2-226-LS | GP-20093 | 2010-01-30 22:49 | Valve lost power due to storms
226-LS | BON_DUR_ROBV362.25 | ROBV 362.2 ac voltage fail..and...maint. alert | 28" line Greenville Sta to OK line | 2-226-LS | GV-21650 | 2010-07-18 22:07 | Storms in area temporary power outage
227-LS | PAL | Building temp. high. | 28" Line Palestine Sta To GVL Sta | 2-227-LS | GV-19729 | 2009-05-31 21:13 | FOUND BLOWER MOTOR NOT RUNNING, FOUND BAD CAPACITOR, GOT FAN RUNNING AND LEFT ON, STARTED AIR COND. AND COOLED OFF BUILDING, REPLACED CAPACITOR FOR FAN
231-LS | GRP | flasher at grapevine seemes to go in and out | 12" Greenville to HWY 75 | 2-231-LS | GV-18458 | 2008-05-20 18:11 | Arlington district took care of this.
231-LS | DAL | Dallas MIP Malfunction did not print on present. Ended batch manually and it printed 2 tickets | 12" Greenville to HWY 75 | 2-231-LS | GV-18460 | 2008-08-06 17:33 | Arlington district took care of this.
231-LS | GVL | Omni Hmi fail, also messed up and printed two tickets but recored no batch size | 12" Greenville to HWY 75 | 2-231-LS | GV-18754 | 2008-09-29 22:30 | No Omni for Location 231. Omni at Greenville printing and working OK
231-LS | RCH_CTJ_ROBV039.49 | At MP 39.5 keep getting Maint. Alert alarm. | 12" Greenville to HWY 75 | 2-231-LS | GV-19601 | 2009-04-10 10:04 | This is in the Arlington District Jeramy Welch work on the wiring problem the the float switch and repaired it.
231-LS | RCH_CTJ_ROBV030.47 | maint alert alarm s03 m.p. 30.5 Account #: 231 | 12" Greenville to HWY 75 | 2-231-LS | GV-19604 | 2009-04-20 21:52 | Found impeller on pump was not turning when motor came on. removed pump reset impeller and reinstalled works good now.
231-LS | RCH_CTJ_ROBV039.49 | BLK VLV 39.5. Seal leak alarm, then "normal", seal leak alarm, then "normal". repetitive alarms. ... Called tech to check it out. | 12" Greenville to HWY 75 | 2-231-LS | AR-2332 | 2009-11-06 13:43 | found bad wiring in conduit replaced and tested
231-LS | RCH_CTJ_ROBV030.47 | Maint. Alert - M.P. 30.5. Called EMT to check out. | 12" Greenville to HWY 75 | 2-231-LS | GV-20847 | 2010-02-09 14:16 | It has been raining all day. Found the pump float had moved slightly and hung up, causing the water to rise to the first level alarm. Also the water being pumped out would go right back in when rthe pump shut off thru the discharge due to the water not running off and just pooling right their. Fixed float. Dug trench for water run off. OK now.
231-LS | RCH_CTJ_ROBV030.47 | robv 30.5 maint. alert alarm @ 2043 J. Patterson called and on way | 12" Greenville to HWY 75 | 2-231-LS | GV-20855 | 2010-02-17 02:51 | Found the sump pump running but not pumping. Will need to pull pump in the morning. OK for now no water coming in right now. Pulled pump found impeller loose on shaft. tightened and tested works good noe.
231-LS | RCH_CTJ_ROBV039.49 | robv 39.5 Maint. Alert alarm | 12" Greenville to HWY 75 | 2-231-LS | GV-23229 | 2011-08-16 21:14 | Notified CCT that the valve in question was in the Arlington area. CCT will make a new TMA.
231-LS | RCH_CTJ_ROBV039.49 | R.O.B.V 39.5 valve control is in Fault, showing A.C voltage fail | 12" Greenville to HWY 75 | 2-231-LS | GV-23737 | 2012-02-27 12:46 | ROBV @ MP 39.5 belongs to ARL area and has been passed off to EMT covering this area.
231-LS | RCH_CTJ_ROBV030.47 | The Product Temperature for the ROBV at 12" M.P. 30.5 is reading a low value (approx. -13 degF). ... EMT Called Out: NONE | 12" Greenville to HWY 75 | 2-231-LS | GV-24408 | 2013-05-08 20:06 | Malfunction sent to wrong area. Reported malfunction to Jeramy Welch for repair.
322-LS | BON_DUR_ROBV362.25 | b/v 362.2 ac voltage fail alm | 28" Texas state line to Allen Sta | 2-322-LS | GV-18028 | 2008-04-24 20:45 | I it was a power company problem. Spoke with Southeastern Electric and they had lost power in the area. They had it restore in about two hours. BV voltage ok.
323-LS | GLN | OUT STATION GRAVITY IS LOCKED UP | 28" line Allen Station to Glenpool | 3-323-LS | GP-14179 | 2007-08-07 05:36 | REPLACED PROCESSOR IN GLENPOOL OUTSTATION PLC
323-LS | HOL_OKM_ROBV493.10 | ROBV - 493.1 had intermintent comm loss and finally went to "FAULT". VLV stayed open. | 28" line Allen Station to Glenpool | 3-323-LS | GP-20233 | 2009-03-28 20:53 | problem solved, closed by admin
323-LS | GLN | lost out staion grav at 14:49 | 28" line Allen Station to Glenpool | 3-323-LS | GP-22089 | 2011-07-04 18:05 | UPS had died. Bypass to regular power. Will replace on Tuesday.
323-LS | HOL_OKM_ROBV493.10 | ROBV 493.1 Maint Alert, AC Voltage Fail. EMT Called Out: Dennis Roling | 28" line Allen Station to Glenpool | 3-323-LS | GP-22881 | 2012-05-23 12:21 | data loss due to power outage. reset with communications D Roling
323-LS | HOL_OKM_ROBV493.10 | ROBV 493.1 Comm's in and out. | 28" line Allen Station to Glenpool | 3-323-LS | GP-23082 | 2012-08-10 04:43 | NO power in panel, reset the Battery Charger Breaker and Engaged the System reset, came back online, called and verified operation with CCT.
326-LS | GLN_CLA_ROBV009.82 | ROBV, seal mp 9.8 @1735 | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-15029 | 2008-01-03 23:44 | Removed product from seal pot. Did not see any more flowing in.
326-LS | GLN_CLA_ROBV009.82 | 1735 ROBV 9.8, seal fail | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-15030 | 2008-01-03 23:47 | Removed product from seal pot. Did not see any more flowing in.
326-LS | HOU_CON_MOBV092.20 | Block valve at MP 92.2 appears to have lost power. Valve locked out on 11/06/08. Lost A/C power on 11/05/08. | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-16650 | 2008-11-17 17:31 | Went to location on 11/11/08. Breaker on incoming main had tripped due to recent storms. Also found (4) other breakers tripped, one in the incoming power cabinet and (3) in the scada cabinet. Reset all breakers but Scada pack was still dead. Marcus had me push the local reset button and evrerything came back to life. Dispatch still could not see status of valve, Comm was still down. No-one was available to troubleshoot problem so I returned to valve on 11-19-08 so that Greg Wagnon could check comms. I arrived at Valve at 1500 and called Greg. Greg was able to ping into the Scada pack so he conferenced in the dispatcher to see if they were getting Valve Status. Dispatch reported that at 1445 the Communication had been re-established and he could see valve status again.
326-LS | HOU_CON_MOBV092.20 | ROBV-92.2 shows fault | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-17735 | 2009-05-20 07:09 | No Power. Found incoming power meter laying on ground. Horses in pasture had rubbed on it and knocked it out of meter base. Replaced meter and reset RTU. Notified Sam Sansone about problem caused by horses.
326-LS | HOU_CON_MOBV092.20 | robv 92.2 going in and out of AC voltage fail | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-19102 | 2010-01-08 01:24 | Checked incoming power on arrival. Was OK. Opened all cabinets to check on Battery Charger and ScadaPack. Found ScadaPack was dead so I changed out the fuse and performed a reset. ScadaPack came back, all alarms cleared.
326-LS | HOU_CON_MOBV092.20 | ROBV-92.2 has no communication. Troubleshoot and repair as needed. EMT Called Out: Dennis Smith | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-20223 | 2010-08-06 19:32 | Power to site good, ScadaPak dead. Pushed Local Reset Button and ScadaPak came back to life. Communications was re-established with Dispatch Center.
326-LS | HOU_CON_MOBV092.20 | ROBV 92.2 - DC Voltage Fail. Valve went into Fault. EMT Called Out: Dennis Smith | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-20425 | 2010-09-23 20:11 | Checked incoming Power and Power check Relay - OK. Checked battery backup system for alarms - none - fan running/power good. Checked Scada Pak - Dead - Performed Local Reset. System reset and all alarms cleared.
326-LS | GLN_CLA_ROBV026.99 | ROBV @ M.P. 27.0 has Maintenance Alert, Valve Control, and AC Voltage Fail. Troubleshoot and repair. Account #: 1 | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-21521 | 2010-06-03 09:00 | John Stock found the fan motor had failed causing the temp to get high and shut down the communications. He replaced the fan the day the malfunction was written.
326-LS | GLN | # 3 falls off on s/u EMT Called Out: John Stock | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-21522 | 2010-07-29 20:50 | John replaced the oil lube switch on unit 3 which was coroded with moisture and repaired the problem
326-LS | HOU_CON_MOBV092.20 | ROBV 92.2 kept going into fault, as AC Voltage Fail. did not call anyone out. Line was down. | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-21528 | 2011-02-03 11:01 | Power fluctuations in this remote area due to weather.
326-LS | HOU_CON_MOBV092.20 | No communications on BLk Valve 92.2 | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-21529 | 2011-02-22 12:56 | Initial visit at 9:00am on Tuesday showed Scada Pak not powered but local AC was present. Hit the Local Reset and restored power to ScadaPak but Satt modem would not power up. Checked voltages on modem power supply, input power was good but output not present. On a second test the output power showed good. Re-plugged into modem but modem would not power up. Doug Ashby called Hughes Sattelite to have a Tech meet me on site. At 18:30 that evening Jason Cook met with me to investigate problem. The modem was still powered down when we opened the cabinet. Jason unplugged and replugged the power supply in and the modem powered up and re-established communications. Jason did not have a DC powered powersupply on his truck so we replaced the original one with an AC powered supply. He ordered a new DC power supply and we will replace the AC unit when this comes in.
326-LS | HOU_CON_MOBV092.20 | robv 92.2 comm loss | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-21964 | 2011-04-25 13:51 | Temporary Comms Fail due to Thunderstorms in area.
326-LS | HOU_CON_MOBV092.20 | ROBV 92.2 comm fail | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-21966 | 2011-04-28 10:10 | ScadaPak was powered down when I arrived. Did a local reset to restore power to ScadaPak. Dispatcher put Station back on scan. I did notice that there was a puddle of water in the bottom of the cabinet. The only source of entry I could see might be the fan unit attached to side of cabinet. We had heavy rainstrorms in the area prior to the malfunction.
326-LS | HOU_CON_MOBV092.20 | ROBV 92.2 Comm outage | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22069 | 2011-06-02 13:43 | Scada Pak down - Local Reset corrected problem.
326-LS | HOU_CON_MOBV092.20 | ROBV 92.2 comm's is out. | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22070 | 2011-06-05 08:21 | Same conditions as before, no storms in area. Working with Sam Samsone to identify intermitant problem. Did clean both air filters and replace.
326-LS | HOU_CON_MOBV092.20 | Block valve 92.2 comm out | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22074 | 2011-06-14 12:35 | Comm fail due to power outage. Measured back-up battery voltage (unloaded) and found batteries reading only 22.78Vdc. Replaced backup batteries and tested system by tripping main AC power breaker. Comms continued to work and Dispatcher able to see all alarms.
326-LS | GLN_CLA_ROBV026.99 | ROBV 27.0 ... While inspecting ROBV with BGannon, he put vlv in "test", Bob did his sequencing and cycling of vlv and all worked fine. When I did mine from CC, he put it in "test" then I "enable" and then I gave vlv closed command. Vlv would not go closed. Had Marcus check things here in CC and SCADA and we couldn't find anything wrong here. | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22458 | 2011-11-22 22:00 | Replaced bad revering contactor.
326-LS | GLN_CLA_ROBV026.99 | lost comms to ROBV 27.0 EMT Called Out: John Stock | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22704 | 2012-03-12 01:07 | Found Faulty Watched Dog Timer and replaced with new watch dog timer
326-LS | GLN_CLA_ROBV026.99 | ROBV 27.0 comm loss EMT Called Out: John Stock | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22794 | 2011-10-14 15:23 | Reset RTU
326-LS | HOU_CON_MOBV092.20 | ROBV 92.2 HAS NO COMM | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22885 | 2012-05-18 20:06 | Local Reset.
326-LS | HOU_CON_MOBV092.20 | Comm loss ROBV 92.2 | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22945 | 2012-05-22 22:21 | Pushed Local Reset to enable comms again. Called Sam Sansone to get input on solution. Sam said he would program a new PLC and we could put it in next time there was a comm fail.
326-LS | HOU_CON_MOBV092.20 | M.P 92.2 Block Valve Comm out | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-22946 | 2012-05-29 19:09 | Met with Sam Sansone and Chris Meyer on site to repair and troubleshoot. Installed new ScadaPak PLC and (3) relays in the failsafe circuit. Tested backup battery system and overvoltage crowbar unit. Checked timing on Brentek watchdog timer. Also checked all grounds on and in cabinets.
326-LS | HOU_CON_MOBV092.20 | Comm Fail going in and out at ROBV 92.2 EMT Called Out: Doug Ashby | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-23179 | 2012-09-06 16:35 | Met with Hughes Sattelite Technician on site, Hughes Tech replaced transmitter on antenna and re-aligned dish.
326-LS | GLN_CLA_ROBV026.99 | ROBV 27.0 AC VOLTAGE EMT Called Out: John Stock | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-23186 | 2012-09-05 20:41 | Power Company having problems
326-LS | GLN_CLA_ROBV026.99 | ROBV 27.0, when testing with Bob Gannon, was able to stop but not open. Valve control went back into "DISABLE" automatically | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-23288 | 2012-10-28 22:27 | Went to ROBV MP27.0 and tested valve. Checked it in local, closed and open valve then had CCT close, stop, and open valve everthing worked OK.
326-LS | GLN_CLA_ROBV026.99 | Loss of comm's to ROBV 27.0 EMT Called Out: Paul Spangler | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-23436 | 2012-09-01 15:40 | Power company having outages
326-LS | GLN_CLA_ROBV026.99 | ROBV 27.0 ac voltage fail, comm out and valve control alarm. EMT Called Out: Paul Spangler | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-23437 | 2012-09-02 21:56 | Power company having outages
326-LS | GLN_CLA_ROBV026.99 | AC Voltage fail at ROBV 27.0 | 24" Glenpool Sta to MO State Line | 3-326-LS | GP-23440 | 2012-12-27 01:53 | Adjusted AC fail relay.
333-LS | GLN | LOAD PIN INDICATOR DOWN POSITION WILL NOT LIGHT UP, BULB HAS BEEN CHANGED | 28" Line Glenpool Sta to West Tulsa | 3-333-LS | GP-15275 | 2008-03-20 18:01 | Replced contact block in Microswitch
333-LS | GLN | VALVE 1305 WILL NOT OPEN INSIDE OR OUTSIDE HAD TO FLOW THROUGH LAUNCHER. | 28" Line Glenpool Sta to West Tulsa | 3-333-LS | GP-16027 | 2008-07-15 10:07 | Found high resistance on auto side of hand/auto switch. Removed, cleaned and replaced contacts in switch. Resistance reading ok. Operational test ok.
333-LS | GLN | when lined up to launch a ball to west t we are getting unrequested movement alarms on S1305 | 28" Line Glenpool Sta to West Tulsa | 3-333-LS | GP-20239 | 2009-11-17 00:42 | Replaced and adjusted and limit switch that acted flaky when tested with a meter and it wasnt close enough to the target.
333-LS | GLN | WHEN SWITCHING FROM W.TULSA BACK TO TANKAGE-GOT A MAGELLAN GLENPOOL WEST LEVEL-2 ALARM WHICH SHUT DOWN THE SOUTH LINE. | 28" Line Glenpool Sta to West Tulsa | 3-333-LS | GP-23109 | 2012-07-03 14:16 | Line shut down while testing new communications equipment with Magellan
336-LS | TUW | B/V 103 shows travel | 16" West Tulsa Sta to Sinclair Ref. | 3-336-LS | GP-23432 | 2012-11-27 11:53 | Repaired limit switch bracket
336-LS | TUW | B/V 103 shows travel | 16" West Tulsa Sta to Sinclair Ref. | 3-336-LS | GP-23433 | 2012-11-27 11:54 | Repaired limit switch bracket ( Duplicate malfunction report)
336-LS | TUW | sump level rising 3' to 6' in six hours EMT Called Out: John Stock | 16" West Tulsa Sta to Sinclair Ref. | 3-336-LS | GP-23498 | 2013-01-03 07:43 | Checked all drain valves and vents to sump. Flushed trap drain valve and pumped sump. Checked with CCT at 0700 sump still empty.
421-LS | HOU_CON_MOBV092.20 | Power Outage @ ROBV 92.2 | 24" OK State Line to Sarcoxie Jct. | 3-421-LS | GP-19349 | 2010-03-23 19:24 | Opened 1st cabinet where ScadaPak is. Found Scadapak not functioning / no lights or activity. Checked fuse mounted on ScadaPak, found good. Hit the Local Reset button. ScadaPak restarted. Called Dispatch, they reported good numbers.
421-LS | HOL_OKM_ROBV493.10 | ROBV 493.1 communication-- line failure | 24" OK State Line to Sarcoxie Jct. | 3-421-LS | GP-20092 | 2010-01-30 17:27 | This malfunction was charged to wrong location tag, malfunction was due to temporary power loss at valve site.
421-LS | HOU_CON_MOBV092.20 | ROBV 92.2 com fail | 24" OK State Line to Sarcoxie Jct. | 3-421-LS | GP-22814 | 2012-04-05 18:51 | Checked incoming power, Battery Backup System, found Scada Pak not functioning. Pushed the Local reset Button and system came back on line. Dispatcher reported everything to be working and no alarms.
426-LS | WEL_STP_ROBV362.88 | Block valve at MP 362.9 has lost comm's. Lost on 11/12/08. | 24" Springfield Sta to Illinois | 4-426-LS | WR-17243 | 2008-11-17 17:27 | Had to do a local reset to restart system. Verified good comms.
426-LS | STP_WDR_ROBV379.59 | ROBV 379.6 Communcations ----line failure | 24" Springfield Sta to Illinois | 4-426-LS | WR-21140 | 2010-11-24 18:56 | Had to reset Hughes satellite box.
435-LS | STL | Valve B-101 shows intransit | 14" IL Line to St. Louis Meter Sta. | 4-435-LS | WR-19481 | 2010-02-09 22:23 | Found actuator motor to be bad. Replaced motor & returned to service.
435-LS | STL | prover not working--no trial or full prove | 14" IL Line to St. Louis Meter Sta. | 4-435-LS | WR-19808 | 2010-01-08 01:36 | Ran 2 trials & 3 complete proves w/o incident ....
438-LS | STL | Valve B-113 shows in transit | Two 14" St. Louis Meter to JD St | 4-438-LS | WR-19602 | 2010-02-09 22:34 | Valve had thawed out and was able to close on next delivery
521-LS | STP_WDR_ROBV379.59 | ROBV 379.6 communication keeps going in and out. | 24" MO State Line to Woodriver Sta | 4-521-LS | WR-19933 | 2010-05-12 09:39 | Heavy storms were in the area. Cleared up in morning and didn't have any problems with comms.
521-LS | STP_WDR_ROBV379.59 | Block valve 379.6 will not open. EMT Called Out: Nick Sullivan | 24" MO State Line to Woodriver Sta | 4-521-LS | WR-22082 | 2011-07-30 10:45 | Duplicate W.O. Corrective action same as WR-22083
521-LS | WDR | Preview gravitometer not working and did not receive a preview sphere alarm. ... EMT Called Out: NONE | 24" MO State Line to Woodriver Sta | 4-521-LS | WR-23507 | 2013-05-20 15:42 | New batteries in UPS and system back on UPS power.
522-LS | WDR_DEC_ROBV411.26 | ROBV @ M.P. 411.3 - RECEIVING ABNORMAL BACK TO NORMAL ALARMS EVERY 2 TO 3 MINUTES. | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-14929 | 2007-08-05 05:46 | Found water and faulty connection in conduit pull box at stem seal leak detection unit switch wiring. Did not have seal pouring materials on site. Will pour seal ASAP to prevent re-occurance.
522-LS | DEC | Decatur dra pump has no flow | 24" Wood River Sta to Decatur Sta | 4-522-LS | HA-14080 | 2008-11-24 14:22 | Roho replaced meter.
522-LS | WDR_DEC_ROBV411.26 | robv 411.3 comm. loss | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-21964 | 2011-04-25 13:51 | Thunderstorms in area affecting satellite dish reception.
522-LS | WDR_DEC_ROBV411.26 | AC voltage fail at 411.3 ... Maint alert at 411.3 ... Valve control at 411.3 EMT Called Out: Nick Sullivan | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-22177 | 2011-09-03 22:02 | Power was restored by power company.
522-LS | DEC | Decator has a dra malfunction alarm it has been running fine till now it has a sp of .5 and is running 1.0 | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-22203 | 2010-02-22 18:46 | This should have been written to Decatur station (Hammond Area). Talked to Ed about this and he took care of what ever DRA system adjustment that was needed at the time of this malfunction.
522-LS | DEC | Decatur, DRA flow is 3 times the set point. | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-22204 | 2010-08-23 17:50 | This should have been written to Decatur station (Hammond Area). Talked to Ed and he made the necessary DRA system adjustments to take care of this at the time of the malfunction.
522-LS | DEC | Decatur TMX on high Nick notifid and will pump in AM | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-22829 | 2012-07-24 02:16 | Tank was sucked out.
522-LS | WDR_DEC_ROBV411.26 | ROBV 411 AC Voltage Fail EMT Called Out: Rogelio Berumen | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-23272 | 2013-01-18 14:51 | AC fail PLC went into protection mode. Reset and started up OK
522-LS | DEC | dra will not run EMT Called Out: David Hagen | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-23424 | 2013-03-24 06:46 | ran pump in manual per CCT, remote set point was inactive due to proximity of incoming batch.
522-LS | DEC | Discharge s/d pump at 778psi | 24" Wood River Sta to Decatur Sta | 4-522-LS | WR-23425 | 2013-03-24 06:48 | found loose wire & bad splices in SCC cab related to M/L pressure switches. Also found pressure switches set low. replace wiring, tightened connections & reset switches.
528-LS | ESH | Fresh Staining from Weep hole on BP 101 at shell Jct. | 12" Line Shell Junction to Shell | 4-528-LS | WR-21142 | 2010-12-07 16:43 | This was from rain getting into the yoke tube and draining out. Will continue to monitor for anything further.
528-LS | ESH | FOR ADMINISTRATIVE PURPOSES Repeated Shell Station Remote Radio Comms Fail. | 12" Line Shell Junction to Shell | 4-528-LS | WR-23443 | 2013-03-24 21:58 | Closing out w/o. Not currently an issue.
529-LS | WDR | Coupon machine at COP terminal would not raise coupon. EMT Called Out: Randy Vinyard | 12" Wood River to Conoco-Hartford | 4-529-LS | WR-22822 | 2012-07-01 12:24 | Coupon holder removed from service for repairs. Disassembled, lubricated and reassembled. Leak tested in shop and put back in at COP. Will be ordering set of original coupon (hardware) as this may have been changed at some point in time causing a tighter fit when rolling coupon in or out.
532-LS | ESL | Grvty no flow alarm. ... EMT Called Out: Rogelio Berumen | 14" E St. Louis Sta to Sun-Mobil | 4-532-LS | WR-23167 | 2012-11-10 13:58 | Bad phone line, repaired by AT&T.
533-LS | ESL | out station gravity-not working | 14" Wood River Sta to E St Louis | 4-533-LS | WR-14557 | 2007-06-11 04:23 | Found the program in the Signal Converter had lost some of it's parameters. Reprogrammed and checked with CCT that he was getting correct reading. No signs of anything wrong, other than a possible power outage.
533-LS | ESL | Gravitometer at ESL station not working. It is reading 38.4 while 60.0 gas is going by. Also, the ESL out-station gravitometer is off by about 4 degrees. | 14" Wood River Sta to E St Louis | 4-533-LS | WR-15893 | 2008-02-16 12:38 | flushed gravitometer loop @ esl and calibrated signal loop for preview and in station gravity. both reading correctly now.
533-LS | ESL | 14" control valve leaking out the bottom into drain. | 14" Wood River Sta to E St Louis | 4-533-LS | WR-19463 | 2009-10-14 23:28 | Cleaned hydraulic cylinder shaft going over paint when stroking
533-LS | ESL | Out station gravity reading 1.4 degrees higher than station gravity. Out sta. 58.8, In sta. 57.4. | 14" Wood River Sta to E St Louis | 4-533-LS | WR-20578 | 2010-08-10 10:19 | flushed out gravitometer tube.
533-LS | ESL | Out station gravitometer reading 7.4 deg. EMT Called Out: David Hagen | 14" Wood River Sta to E St Louis | 4-533-LS | WR-21530 | 2011-02-14 19:06 | Found AT&T data line down. Called AT&T and they repaired issue.
533-LS | ESL | Preview Gravitomter not tracking. | 14" Wood River Sta to E St Louis | 4-533-LS | WR-22012 | 2011-04-28 22:57 | Flushed Gravitometer & is now tracking..
533-LS | ESL | 14" Preview Gravitometer losing comms; and not tracking accurately EMT Called Out: Randy Vinyard | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23103 | 2012-11-01 01:49 | Checked out problem. Called in a trouble ticket to AT&T for an in and out data circuit. Dave Hagen will be handling this malfunction from this point.
533-LS | ESL | out station gvty giving erratic values. | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23159 | 2012-11-06 06:43 | data line repaired by AT&T
533-LS | ESL | TEST LEADS NEED REPAIRED @ MP. 12.8 EMT Called Out: David Hagen | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23165 | 2012-12-10 15:30 | extended conduit & wired up test station.
533-LS | ESL | Preview Gravitometer to ESL is erratic. EMT Called Out: David Hagen | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23275 | 2013-01-14 02:38 | replaced motor & pump.....
533-LS | ESL | east st louis out station gravotometer is not working EMT Called Out: Rogelio Berumen | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23426 | 2013-03-30 23:11 | Found fault in AT&T data ckt. trouble shot & repaired with AT&T tech.
533-LS | ESL | outstation gravotomer is not working ... EMT Called Out: Rogelio Berumen ... throughput_loss: No | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23829 | 2013-10-14 00:29 | replaced malfunctioning signal converter.
533-LS | ESL | East St. louis preview gravitometer not tracking. ... EMT Called Out: Randy Vinyard ... throughput_loss: No | 14" Wood River Sta to E St Louis | 4-533-LS | WR-23845 | 2013-10-31 03:47 | Solatron converter malfunction, needs repaired / replaced. Verified problems with Dave. He will be handling this from here.
535-LS | ESH | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-10675 | 2005-06-27 13:30
535-LS | ESH | Terminal Boxes and Explosion Proof Housings | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-10677 | 2005-06-27 13:30 | no corrosion found
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11029 | 2005-08-25 15:06
535-LS | ESH | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11030 | 2005-08-25 15:06
535-LS | EAM | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11031 | 2005-08-25 15:06
535-LS | EAM | Back Pressure Relief Valves. Thermal Relief Valves. | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11032 | 2005-08-25 15:07
535-LS | EAM | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11033 | 2005-08-25 15:07
535-LS | ESH | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11034 | 2005-08-25 15:07
535-LS | EAM | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11035 | 2005-08-25 15:07
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11180 | 2005-09-25 12:44
535-LS | ESH | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11181 | 2005-09-25 12:44
535-LS | ESH | Back Pressure Relief Valves. Thermal Relief Valves. | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11182 | 2005-09-25 12:44
535-LS | ESH | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11183 | 2005-09-25 12:44
535-LS | ESH | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11184 | 2005-09-25 12:44
535-LS | EAM | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11373 | 2005-10-25 19:15
535-LS | ESH | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11374 | 2005-10-25 19:15
535-LS | EAM | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11375 | 2005-10-25 19:15
535-LS | ESH | Back Pressure Relief Valves. Thermal Relief Valves. | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11376 | 2005-10-25 19:16
535-LS | EAM | Back Pressure Relief Valves. Thermal Relief Valves. | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11377 | 2005-10-25 19:16
535-LS | ESH | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11378 | 2005-10-25 19:16
535-LS | EAM | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11379 | 2005-10-25 19:16
535-LS | ESH | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11380 | 2005-10-25 19:16
535-LS | EAM | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11523 | 2005-11-25 20:48
535-LS | ESH | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11524 | 2005-11-25 20:49
535-LS | EAM | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11525 | 2005-11-25 20:49
535-LS | ESH | Back Pressure Relief Valves. Thermal Relief Valves. | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11526 | 2005-11-25 20:49
535-LS | ESH | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11527 | 2005-11-25 20:49
535-LS | ESH | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11528 | 2005-11-25 20:49
535-LS | EAM | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11529 | 2005-11-25 20:49
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11657 | 2005-12-25 19:32
535-LS | ESH | Protective Devices, Pressure switches, Time delays | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11658 | 2005-12-25 19:32
535-LS | ESH | Back Pressure Relief Valves. Thermal Relief Valves. | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11659 | 2005-12-25 19:32
535-LS | ESH | Station Valves 4" or Larger | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11660 | 2005-12-25 19:32
535-LS | ESH | Sump, Oil Water Separator System | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11661 | 2005-12-25 19:32
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11857 | 2006-01-25 20:46 | Lighing out, will plan repairs
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-11974 | 2006-02-25 18:29 | Lighing out, will plan repairs
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-12114 | 2006-03-25 15:24 | Out, Will plan repairs
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-12448 | 2006-05-25 17:49 | known lights out
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-12588 | 2006-06-25 18:00 | known light out
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-12809 | 2006-07-25 13:01 | known lights out
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-12949 | 2006-08-25 12:14 | known lights out
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-13087 | 2006-09-25 15:53 | known lights out
535-LS | ESH | Area Lighting | 12" Line Shell Jct to Ar-Am Jct | 4-535-LS | WR-13262 | 2006-10-25 18:59 | known lights out
537-LS | ESL | Meter 34 pre-amp fail | 14" E. St. Louis Sta to MO Line | 4-537-LS | WR-20068 | 2010-06-03 16:26 | replaced k3 relay on S1 board. This cleared alarm & also induced a pre-amp fail alarm & was able to clear via reset push button.
537-LS | ESL | Relief line flow alarm , s/d 14". | 14" E. St. Louis Sta to MO Line | 4-537-LS | WR-20586 | 2010-09-07 04:27 | Replaced faulty limit switch on Brodie relief valve.
537-LS | ESL | In station Gravitometer is jumping all over and giving a alarm EMT Called Out: Nick Sullivan | 14" E. St. Louis Sta to MO Line | 4-537-LS | WR-23038 | 2012-09-30 00:05 | flushed & replaced amp.
537-LS | ESL | In station control valve malfunctioned on start up to (PHI, B-105). Resulted in 14' S/D. EMT Called Out: Randy Vinyard | 14" E. St. Louis Sta to MO Line | 4-537-LS | WR-23348 | 2013-02-26 10:42 | Controller was "locked up". Would not open or move control valve in auto. Pulled Toshiba controller and re-seated into backplane to "reset". Tested for proper operation.
523-LS | DEC_CHA_ROBV541.58 | ROBV 541.6 AC Voltage fail ... Maint. alert ... valve control fault | 24" Decatur to Peotone Meter Sta | 5-523-LS | HA-15331 | 2009-11-23 20:18 | Sight lost power, power was restored.
523-LS | DEC_CHA_ROBV541.58 | ROBV 541.6 could not close remotely. | 24" Decatur to Peotone Meter Sta | 5-523-LS | HA-17627 | 2011-10-20 19:38 | Worked with Steve Nelson and Kraig Caldwell on Enable circuit. Block valve went open and closed also stopped with commands from Tulsa Contol Center once the valve was enabled.
523-LS | HMDAO | 2_keyholderphone: 2191111111 5_action: Issuance requesttype: Key Management 4_keyserialnumber: 999 3_keytypenumber: 1-1 1_keyholdername: ED Drebes/ testing | 24" Decatur to Peotone Meter Sta | 5-523-LS | K-10024 | 2011-12-15 17:12 | Randy and Ed testing and training on system.
523-LS | DEC_CHA_ROBV541.58 | ROBV 541.6 IS IN COMM FAIL WE HAVE TAKEN IT OFF SCAN | 24" Decatur to Peotone Meter Sta | 5-523-LS | HA-18182 | 2012-08-23 18:40 | Replaced SCADA pak with Sam Sansone and Chris Meyer
523-LS | DEC_CHA_ROBV541.58 | M.P 541.6 AC voltage fail alarm EMT Called Out: Ed Drebes | 24" Decatur to Peotone Meter Sta | 5-523-LS | HA-18288 | 2012-11-13 04:11 | Adjusted set point on AC undervoltage relay.
524-LS | PEO | com fail | 24" Peotone Meter Sta to IN line | 5-524-LS | HA-12890 | 2007-08-20 11:36 | Donovan Wilson fixed, not sure what was done to repair. Chris Meyer
524-LS | PEO | Communication Fail | 24" Peotone Meter Sta to IN line | 5-524-LS | HA-15559 | 2010-01-08 01:30 | Ed worked with phone company to repair disconnected line.
524-LS | PEO | Peotone Junction lost communcation with scherville. Will call x3333 | 24" Peotone Meter Sta to IN line | 5-524-LS | HA-18292 | 2012-11-16 18:30 | AT&T technician repair issued.
621-LS | DEC_CHA_ROBV541.58 | ROBV-541.6 showing fault. | 24" Ill. Line to Schererville Jct | 5-621-LS | HA-17845 | 2012-03-07 15:35 | Power company problems because of the high winds. Came back on when power company restored power
621-LS | DEC_CHA_ROBV541.58 | Comm outage at ROBV MP 541.6 | 24" Ill. Line to Schererville Jct | 5-621-LS | HA-18077 | 2012-07-23 11:59 | lost power to scada pack. rebooted and this repaired the malfunciton.
621-LS | DEC_CHA_ROBV541.58 | ROBV 541.6 comm loss and recieved "fault" EMT Called Out: Ed Drebes | 24" Ill. Line to Schererville Jct | 5-621-LS | HA-18117 | 2012-08-05 04:20 | Replaced scada pack with c. meyer.
622-LS | SCH | SCHERERVILLE FLASHER NOT WORKING. IT IS PEGGED AT 250. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-12888 | 2007-12-02 02:02 | Donovan Wilson fixed, not sure what was done to repair malfunction. Chris Meyer
622-LS | SCH | Auto-flasher @ SJ not working corretly. No flash for 15 minutes after jet arrived, now showing 89 flash (in JET). Called Ed Drebes to investigate. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13198 | 2008-02-17 13:44 | A sensors went bad and swapped over to "B". Changed "A" sensors in auto flasher.
622-LS | SCH | RE: AUTO-FLASHER @ SJ. Around 45 minutes into the jet, the auto-flasher is showing a normal flash. After discussion with Ed, we concluded that it probably flushed itself out and is working properly. I will watch the flash closely when it gets to Hammond. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13199 | 2008-02-17 14:16 | Refer to HA-13198
622-LS | SCH | GRAVTIOMETER @ SCHER JUNCTION IS ACTING ERRATIC / GTY READING DROPPING IN SPIKES. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13339 | 2008-05-02 20:24 | Problem is suspected to be caused by the heat in the contol room at Schererville. I found the AC was not working. Once the AC was repaired the problem has not reoccured.
622-LS | SCH | 11;49;50 SCH COMMS FAIL alarm; Heavy rain and strong winds affecting the phone network also; C.C.T. notified | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13342 | 2008-05-11 17:27 | Schererville lost power. Called Nipsco and got power restored.
622-LS | SCH | sump level 4.6 | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13351 | 2008-05-26 23:56 | Sump was rising due to valve packing leak on the hammond valve. Packed valve and the leak stopped.
622-LS | SCH | 13:40 SEVERE THUNDERSTORM THROUGH AREA; PREVIEW GRAVITY INCORRECT AND PREVIEW FLASH READS ZERO - MAINLINE IN JET FUEL - CALLED OUT CHRIS MEYER. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13440 | 2008-06-08 18:54 | Schererville is with out power. B phase tripped a fuse out at main pole at street. Nipsco has been notified twice, and I am awaiting a response to when power will be restored. 6-9-08 Power restored 6-9-08 15:00
622-LS | SCH | SCHERERVILLE COMMS FAIL. CALLED OUT CHRIS | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13576 | 2008-07-01 04:11 | Schererville comms were restored. There was a ticket opened with sprint on the Schererville line.
622-LS | SCH | gravitometer at schererville not working | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-13673 | 2008-08-12 08:24 | Found motor shorted due to single phasing during loss of phase. Replaced pump and motor. 8/13/08 C. Meyer
622-LS | SCH | 02:35 SCH JCT PREVIEW AUTO FLASHER; NOT WORKING; C.C.T. reports it as being on. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-14097 | 2008-12-23 10:18 | Refer to HA-14093
622-LS | SCH | PREVIEW AUTOFLASHER; C.C.T. SAY'S IT'S ON BUT IT IS NOT WORKING - ORIGINAL MALFUNCTION ON 12-23-08. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-14227 | 2009-01-08 20:53 | Auto flasher is shut off due to heater not working in the sample building. It will be put back in service as soon as heater is fixed.
622-LS | SCH | During N/L to 18 grade interface, no sphere was indicated at Scher. CCT did not see sphere indication either. Sphere DID come in to Hammond. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-14550 | 2009-03-24 08:50 | Checked for alarms, but everything looked ok. Will keep an eye on and if problem reoccurs pig-sig will be pulled and checked.
622-LS | SCH | Hammond Block valve (B101) shows to be in-travel while in the closed position. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-14757 | 2009-06-09 07:33 | Refer to HA-14915
622-LS | SCH | Valve B-101 failed to close. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-14997 | 2009-08-03 12:28 | Refer to HA-14998
622-LS | SCH | Valve B101 will not open | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-14998 | 2009-08-04 07:04 | Replaced drive nut and bearings in the valve gearbox.
622-LS | SCH | Val. b101 would not open to HMD | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-15086 | 2009-08-15 00:27 | Replaced drive bushing and bearings in valve gearbox.
622-LS | SCH | Valve B-101 @ Schererville Jct. apparently not holding pressure. Pressure continues to rise @ Hammond while valve is closed. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-15227 | 2009-09-20 00:16 | Valve is schedualed to be replaced next year.
622-LS | SCH | Valve B-101 @ Schererville Jct. apparently not holding pressure. Pressure continues to rise @ Hammond while valve is closed. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-15237 | 2009-10-16 05:05 | Valve is schedualed to get replaced next year.
622-LS | SCH | Schererville flasher fail alarm | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-15740 | 2010-03-16 13:33 | Replaced philaments A and B in Auto-Flasher.
622-LS | SCH | Flasher not working. | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-17080 | 2011-02-06 01:42 | No air flow on alarm condition. Adjusted needle valve to achieve correct air flow through system. Alarm then cleared.
622-LS | SCH | MAIN LINE PREVIEW FLASH IS SHOWING 250 HAD CCT TURN BACK OFF AND BACK ON TO SEE IF WOULD RESET BUT DID NOT . | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-17081 | 2011-02-06 00:41 | Multiple Malfunctions.
622-LS | SCH | PREVIEW FLASH WILL NOT READ ONLY READS 250 HAD CCT TURN OFF AND BACK ON . | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-17094 | 2011-02-25 17:59 | fill timeout alarm, configured system and recieved a good flash.
622-LS | SCH | Valve B-101 would not open on switch from WDR to HMD. Valve would show travel, then time out. Troubleshoot and repair EMT Called Out: Chris Meyer | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-17394 | 2011-05-04 05:56 | Valve torqued out do to differential pressure. CCT's have been directed to keep the pressure at schererville below 175 PSI to avoid this problem. New bearings have been ordered to try and help the torque needed to open the valve. The acctuator was replaced and the valve malfunction has been fixed.
622-LS | SCH | PREVIEW FLASHER NOT WORKING HAD CCT TURN ON AND TURN OFF AND STILL WONT WORK | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-17445 | 2011-06-19 06:19 | changed A sensors and auto flasher is working normally.
622-LS | SCH | Flasher reading was a steady 143 deg. while gas was passing. EMT Called Out: Jacob Smithson | 24" Schererville Jct to Hammond Sta | 5-622-LS | HA-17525 | 2011-08-09 19:42 | Replaced vaccum pump and a sensors. Made adjustments. Will keep an eye on the flasher and make adjustments as need be. C. Meyer
630-LS | COL | COL JCT METER READING FLOW RATE OF -1876, GTY READING 5.8, NET BBLS NOT COUNTING. WE ARE RUNNING TO PHILLIPS AT 9560 FLOW RATE. | 16" Phil-Tex Jct to Phillips | 5-630-LS | HA-17905 | 2012-04-08 23:57 | Meter was removed from piping so that COL Jct could be painted. This is not a malfunction.
630-LS | COL | METER PROBLEM @ COLUMBUS JUNCTIN TO PHI (B101) ... EMT Called Out: NONE ... throughput_loss: Yes | 16" Phil-Tex Jct to Phillips | 5-630-LS | HA-18822 | 2013-10-16 10:54 | DUPLICATE MALFUNCTION
635-LS | ECH | gravitometer @ ech station is not reading dt301 | 14" Hammond Sta to E Chicago Jct | 5-635-LS | HA-16064 | 2010-06-11 05:40 | Refer to HA-16069
635-LS | ECH | CCT HAS COMMS BUT WE DO NOT CANNOT SEE VALVE STATUS BUT CCT CAN ... EMT Called Out: Jacob Smithson | 14" Hammond Sta to E Chicago Jct | 5-635-LS | HA-18675 | 2013-07-17 19:47 | MNET module in East Chicago RTU was not communicating with backplane. I reseated the module and this repaired the malfunction.
635-LS | ECH | East Chicago Comm Fail. Hasn't cleared itself for several hours. ... EMT Called Out: NONE | 14" Hammond Sta to E Chicago Jct | 5-635-LS | HA-18776 | 2013-10-01 12:44 | worked with Roni C. on going issue he is working with an outside group to resolve problem.
636-LS | COL | Valve B101 will not open remotely until it is cycled manually. This happens periodically. | 16" Hammond Sta to Phil-Tex Jct | 5-636-LS | HA-18131 | 2012-08-24 15:07 | Had talks with engineering to find out that valve at Columbus will not open until back pressure valve is in correct state. Once operator lines up operations in correct order valves can be opened with no problems. This repaired the malfunciton.
636-LS | COL | Hammond Tech informed John Majewski of comm issues at Columbus Jct. Checked with comms desk and they informed CCT that there is good comms at Col Jct. ... EMT Called Out: Jacob Smithson | 16" Hammond Sta to Phil-Tex Jct | 5-636-LS | HA-18515 | 2013-04-12 06:20 | HAD TO DOWNLOAD PLC PROGRAM WORKED WITH RONI AND CHRIS THE REPAIRED THE MALFUNCTION
636-LS | COL | COLUMBUS JCT NOT IN AUTO | 16" Hammond Sta to Phil-Tex Jct | 5-636-LS | HA-18518 | 2013-04-15 03:48 | had to reload the plc program worked with roni and chris. this repaired the malfunction
636-LS | COL | B101 WILL NOT OPEN OR CLOSE . ... EMT Called Out: Jacob Smithson | 16" Hammond Sta to Phil-Tex Jct | 5-636-LS | HA-18677 | 2013-07-21 17:32 | Found bad control transformer on Limitorque operator. Replaced transformer and associated fuses. This repaired the malfunction.
636-LS | COL | ULtra Sonic meter is counting bbls while line is down ... EMT Called Out: NONE ... throughput_loss: No | 16" Hammond Sta to Phil-Tex Jct | 5-636-LS | HA-18823 | 2013-10-18 11:36 | Duplicate malfunction
636-LS | COL | Hammond to Columbus Junction is showing an overage on the ultra sonic meter. Columbus is showing flow while the line is shut down. ... EMT Called Out: NONE ... throughput_loss: No | 16" Hammond Sta to Phil-Tex Jct | 5-636-LS | HA-18828 | 2013-10-26 03:31 | THE POWER SUPPLY WAS NOT WORKING PROPERLY. REPLACED POWER SUPPLY CARD THIS REPAIRED THE MALFUNCTION.
637-LS | COL | Flush All Identified Dead Legs | Phil-Tex Jct/16" to Texaco | 5-637-LS | HA-17668 | 2011-11-25 14:15 | P00028A - Flush All Identified Dead Legs: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check Sheets 371 Flush All Lines to Pressure Transmitters Switches and Dead Legs [ ] Pass [ ] Fail Comment:___________________________________
638-LS | BDG | REMOTE VALVE B-109 TO BUCKEYE TF (NORCO) AT WEST SHORE/BADGER STATION; 4 TIMES FAILED TO OPEN FROM HMI - CALLED DONOVAN AND CHRIS. | 12" E Chicago Jct to Badger Mobil | 5-638-LS | HA-12765 | 2007-12-03 06:56 | Valve opened but failed to indicate status because the radio transmitter was down due to partial power at East Chicago Station. Called NIPSCO out and they restored power to Station. B109 valve cycled properly when power was restored to radio transmitter.
638-LS | BDG | 02:08 B-109 BUCKEYE TANK FARM VALVE AT WEST SHORE BADGER STATION; DID NOT OPEN 3 TIMES FROM HMI; called Chris; was told to call Buckeye Em-Tech; notified Buckeye/NORCO Operator; Buckeye/MORCO Operator went to investigate.. | 12" E Chicago Jct to Badger Mobil | 5-638-LS | HA-12976 | 2008-01-26 08:10 | Valve is not owned by explorer. Problem was that valve was locked out by buckeye.
638-LS | ECH | 19:32 - HA7-HA8 COOMS FAIL (B109) BUCKEYE; Number 2 Unit EAST CHICAGO SHUTDOWN on the preceeding COMMS FAIL while delivering through B-103 to Valero. Restarted Number 2 at 19:33 - no further episodes. | 12" E Chicago Jct to Badger Mobil | 5-638-LS | HA-15325 | 2009-10-29 01:00 | Monitored radios and have not seen anymore outages working with engineering to trouble shoot the issue.
639-LS | ECH | Remote valve B106 to West Shore would not open from the operators HMI or the back-up HMI | West Shore /Two 16" Lines to Shell | 5-639-LS | HA-13661 | 2008-07-27 07:27 | Found WS radio not communicating. Worked with Gilbert on upgrading to new radio. Valve worked when tested. 7/28/08 C. Meyer
639-LS | ECH | After changing West Shore corrosion coupon on BET's north property, I noticed product seeping from the crank. Re-drained coupon tool and Chris came out and removed it and replaced with a plug. | West Shore /Two 16" Lines to Shell | 5-639-LS | HA-16982 | 2011-01-28 19:16 | Replaced holders soft good seals and operator replaced on line, will check for leaks on next startup.
639-LS | ECH | Flush All Identified Dead Legs | West Shore /Two 16" Lines to Shell | 5-639-LS | HA-17669 | 2011-11-25 14:15 | P00028A - Flush All Identified Dead Legs: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check Sheets 371 Flush All Lines to Pressure Transmitters Switches and Dead Legs [ ] Pass [ ] Fail Comment:___________________________________
639-LS | ECH | Recieved numerous ReMote Valve B106 Errors. Valve statues going white. West Shore called and asked why we were opening the valve. They showed the valve in transit. Brian, the West Shore operator said it is not affecting there operations and can be addressed in the morning. EMT Called Out: Jacob Smithson | West Shore /Two 16" Lines to Shell | 5-639-LS | HA-17914 | 2012-04-17 01:06 | Westshore facility lost one phase of power feeding our valve. Disconnected power and restroed when power was restored. This repaired the malfunction.
642-LS | GRF | Station Valves 4" or Larger | 16" Griffith to Tecumseh/Lakehead | 5-642-LS | HA-10166 | 2005-04-25 11:59
643-LS | GRF | Prover keeps aborting | 16" Griffith Meter Sta to ARCO PL | 5-643-LS | HA-12977 | 2008-01-24 17:23 | Lower detector switch has been fixed. Prover was pulled out of service due to a seeping hydraulic ram seal.
643-LS | GRF | prover not working | 16" Griffith Meter Sta to ARCO PL | 5-643-LS | HA-14898 | 2009-07-08 18:54 | Paul found breaker tripped, he reset breaker.
643-LS | GRF | valve x104 would not open | 16" Griffith Meter Sta to ARCO PL | 5-643-LS | HA-14994 | 2009-07-31 10:25 | Found bad wire connection. Replaced relays and fixed wire connection.
644-LS | KND | Flush All Identified Dead Legs | 16" Kennedy Jct to Arco Incl. Jcts | 5-644-LS | HA-17675 | 2011-11-25 14:16 | P00028A - Flush All Identified Dead Legs: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check Sheets 371 Flush All Lines to Pressure Transmitters Switches and Dead Legs [ ] Pass [ ] Fail Comment:___________________________________
645-LS | ECH | No Comm ... EMT Called Out: Willie Rodriguez ... throughput_loss: Yes | 14" Hammond Sta to East Chicago Jct | 5-645-LS | HA-18884 | 2013-12-01 13:22 | Gilbert had Mnet Reset Remotely.
674-LS | GRF | Will not prove. | 16" Griffith Station to Marathon PL | 5-674-LS | HA-12493 | 2007-08-16 09:49 | Donovan wilson has fixed the problem. Not sure what was done to repair the malfunction.
674-LS | GRF | valve x-102 would not open | 16" Griffith Station to Marathon PL | 5-674-LS | HA-13215 | 2008-03-13 06:59 | Terry was called out and found bad wiring to the valve. He fixed the wiring and valve worked correctly.
674-LS | GRF | Valve X103 will not open. Second time in as many days. | 16" Griffith Station to Marathon PL | 5-674-LS | HA-13437 | 2008-06-06 15:00 | Valve was pressure locked. Released pressure and valve opened correctly. Theremal relief was replaced and tested.
674-LS | GRF | Valve X103 will not open; shows valve in-travel status. | 16" Griffith Station to Marathon PL | 5-674-LS | HA-13438 | 2008-06-05 15:07 | Valve was pressure locked. Released pressure and valve opened correctly. Theremal relief was replaced and tested.
675-LS | ECH | Unable to read correct status on Valve B-109 to Norco at East Chicago, Contacted Jacob to verify status. EMT Called Out: Jacob Smithson | 14" East Chicago Junction to Clark | 5-675-LS | HA-18008 | 2012-06-18 18:52 | SCADA maintenace adjusted registers to see indication on valve. This malfunction has been repaired.
675-LS | ECH | Comm Fail. | 14" East Chicago Junction to Clark | 5-675-LS | HA-18184 | 2012-07-29 11:21 | Comms restored after time. This repaired the malfunction.
677-LS | ECH | Scada pac went out ... EMT Called Out: Jacob Smithson | 14" East Chicago to BP White Oak | 5-677-LS | HA-18764 | 2013-09-12 08:24 | Duplicate malfunction. Will close out on duplicate.
677-LS | ECH | Comm's out. Cannot close valves. ... EMT Called Out: NONE | 14" East Chicago to BP White Oak | 5-677-LS | HA-18765 | 2013-09-12 15:58 | Reseated MNET module. This repaired the malfunction.
677-LS | ECH | COMM LOSS ... EMT Called Out: Willie Rodriguez ... throughput_loss: No | 14" East Chicago to BP White Oak | 5-677-LS | HA-18815 | 2013-10-06 17:20 | RE-SEATED MNET CARD RESTORED COM LOSS TO SCADA
222-LS | HOU | Port Arthur outstation gravity out | 28" Line Port Arthur to Houston | 6-222-LS | HU-13586 | 2007-12-19 16:11 | Trudy found signal at Control Center turned off on HMI, activated signal and had a good gravity signal.
222-LS | PTA_HAN_MOBV003.06 | Per VBK inspector, product located in valve stem at VBK at milepost 3.0 E. Hillebrandt Bayou | 28" Line Port Arthur to Houston | 6-222-LS | PA-15057 | 2009-10-25 19:06 | Packed valve and lubricated injector piston bolt
222-LS | PTA_HAN_ROBV008.98 | robv8.98 ac voltage fail | 28" Line Port Arthur to Houston | 6-222-LS | PA-15067 | 2010-08-26 20:08 | I drove to the ROBV and discovered that power was out to the meter. Power was also lost in the neighborhood surrounding the ROBV and rectifier. I notified the power company and power was restored.
222-LS | PTA_HAN_ROBV008.98 | robv 8.98 is in fault condition.. | 28" Line Port Arthur to Houston | 6-222-LS | PA-15438 | 2010-11-06 11:28 | verified with CCT about the problem. Contacted Greg Wagnon and Doug Ashby. All comms and voltages looked good.
222-LS | PTA_HAN_ROBV008.98 | ROBV @ MP 8.98 keeps losing comm's | 28" Line Port Arthur to Houston | 6-222-LS | PA-15439 | 2010-11-15 14:06 | Verified current problem with CCT. The problem was not present when I called. Contacted Doug and Greg and the comm's looked good. They could'nt determine the root cause of the problem.
222-LS | PTA_HAN_ROBV008.98 | ROBV MP 8-98 power goes out and comes back on sporadically. | 28" Line Port Arthur to Houston | 6-222-LS | PA-15440 | 2010-12-03 12:18 | I spoke with Doug Ashby. He informed me that he is looking into the details as to why this is happening. He stated that it is not something that the techs can repair.
222-LS | PTA_HAN_ROBV008.98 | ROBV 8.98 comms keeps going in and out. EMT Called Out: Alan Frazier | 28" Line Port Arthur to Houston | 6-222-LS | PA-15446 | 2010-12-07 14:14 | I spoke with Doug Ashby about this issue. He is looking into why this problem is occurring. He stated that it is not something that the local techs can repair.
222-LS | PTA_HAN_ROBV008.98 | ROBV-8.98 alarming in "Fault" and "AC Voltage Fail". Repair as needed. | 28" Line Port Arthur to Houston | 6-222-LS | PA-15565 | 2011-01-02 10:09 | This is an ongoing issue that I have notified Doug Ashby about. He states that there is nothing that the local techs can do to mitigate the problem. According to Doug an equipment upgrade needs to be performed on the comms equipment. He is not sure when this will take place.
222-LS | PTA_HAN_ROBV008.98 | ROBV @ MP-8.98 keeps going in and out of fault over the past hour. | 28" Line Port Arthur to Houston | 6-222-LS | PA-15570 | 2011-01-08 03:07 | I notified Doug Ashby and he states that the local techs can't mitigate the issue. Doug believes that nothing short of equipment upgrades will repair the issue that comes and goes. Doug is aware of this problem.
222-LS | PTA_HAN_ROBV008.98 | COMM fail @ ROBV 8.98 | 28" Line Port Arthur to Houston | 6-222-LS | PA-16032 | 2011-10-17 21:41 | assisted a tech with HughesNet re-align the sattelite. We also found a bad power supply to the modem. A new power supply is being ordered.
222-LS | HAN | station not in auto, valve actuator fail happened on shut down but station is now running fine EMT Called Out: Derek Freisner | 28" Line Port Arthur to Houston | 6-222-LS | PA-16069 | 2011-11-17 15:04 | MOV 209 was not available. I troubleshot the valve and found that one of the blue connectors on the card with the valve status LCD was unplugged. I plugged the connector back in and the not available went away.
222-LS | PTA_HAN_ROBV008.98 | Tried to closed ROBV 8.98. No control. No movement. EMT Called Out: Alan Frazier | 28" Line Port Arthur to Houston | 6-222-LS | PA-16417 | 2012-08-09 08:22 | troubleshot the valve and found a loosed connection on a jumper. Tightened the loose connection and this solved the problem.
222-LS | PTA_HAN_ROBV008.98 | ROBV 8.98 AC Voltage Fail ... EMT Called Out: Kyle Daniel | 28" Line Port Arthur to Houston | 6-222-LS | PA-16645 | 2013-04-13 13:26 | Power outage due to entergy issues. Valve power resupplied in appoximately 2 hours. Kyle Daniel
245-PS | DELETE | Station Monthly Walkthru PM's | Orange Pump Station | 6-245-PS | PA-16196 | 2012-03-25 17:01 | 245PM00 - Station Monthly Walkthru PM's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items 1. Complete visual check of station.
245-PS | DELETE | Station Monthly Walkthru PM's | Orange Pump Station | 6-245-PS | PA-16243 | 2012-04-25 16:24 | 245PM00 - Station Monthly Walkthru PM's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items 1. Complete visual check of station.
245-PS | DELETE | Station Monthly Walkthru PM's | Orange Pump Station | 6-245-PS | PA-16278 | 2012-05-25 15:00 | 245PM00 - Station Monthly Walkthru PM's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items 1. Complete visual check of station.
245-PS | DELETE | Station Monthly Walkthru PM's | Orange Pump Station | 6-245-PS | PA-16317 | 2012-06-25 14:05 | 245PM00 - Station Monthly Walkthru PM's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items 1. Complete visual check of station.
245-PS | DELETE | Station Monthly Walkthru PM's | Orange Pump Station | 6-245-PS | PA-16371 | 2012-07-25 19:59 | XXX245P - Station Monthly Walkthru PM's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items 1. Complete visual check of station.
245-PS | DELETE | Station Monthly Walkthru PM's | Orange Pump Station | 6-245-PS | PA-16409 | 2012-08-25 18:23 | 245PM00 - Station Monthly Walkthru PM's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items 1. Complete visual check of station.
213-LS | LCR | Power fail EMT Called Out: Richard Hawkins | 10" Lake Creek to Waco | 7-213-LS | AR-4475 | 2011-10-28 18:13 | GENERIC - Generic Malfunction: power falure reset UPS with greg gagnon to return commucations to normal. sent HMI to Sam Sansone hard drive falure
213-LS | LCR | Lake Creek...battery charger fail... and... MOV power fail | 10" Lake Creek to Waco | 7-213-LS | AR-4744 | 2012-03-25 19:05 | check circuits to charger and MOV ...circuits working... local power outage
213-LS | LCR | comm loss at Lake creek station | 10" Lake Creek to Waco | 7-213-LS | AR-5174 | 2012-12-14 00:45 | check station for power loss, checked UPS for faults, check battery charger for faults.contacted Doug Ashby to have com check. CCT (John) had a comm loss indication. talked with Sam Samsone. fault cleared comm loss indication cleared.
214-LS1 | WAC | Waco station Batter Charger Fail--Alarm in HMI | 10" Waco to Ross | 7-214-LS1 | AR-2732 | 2010-03-26 21:56 | re-wired the alarms contacts to the proper configuration, tested ok
214-LS1 | ROS_ARL_MOBV257.08 | Product stain & liquid around plug threads on valve yoke @ Pioneer PKWY mainline block valve. | 10" Waco to Ross | 7-214-LS1 | AR-3745 | 2011-01-21 15:11 | Injected packing, emptied yoke tube & cleaned stain.
216-LS1 | FOR | Valve 03 at Fort Worth on the NoLead valve going to SemFuels shows in transition. Vlv will open, but when closed, will not show closed. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-761 | 2008-08-26 12:33 | Valve would hang up when travelling to the closed position, tripping the torque switch. The pins mounted in the yolk whoud hang up in the guide. The vlve just needed lubrication. It was completely dry. Lubed all valves in the station.
216-LS1 | FOR | Meter 97 @ Fort Worth will not accept changes. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1028 | 2008-06-18 11:06 | Refered to Brian Gasperino. An issue with the OMNI/HMI was corrected
216-LS1 | FOR | Meter 97 gravity keeps going in and out. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1029 | 2008-06-18 11:06 | Parts for repair are unavailable. Searching for complete spare
216-LS1 | ARL | 3" Ft. Worth(Meter #96) gravitometer not working. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1031 | 2008-07-03 21:16 | Unit is not repairable. Searching for replacement.
216-LS1 | ARL | Ft. Worth 3" F/O line gravitometer (Meter #96) still not working. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1034 | 2008-07-10 05:14 | Parts unavailable. Continuing search for replacement
216-LS1 | FOR | FOR 6" Meter 97 gravity not working. Lots of alarms and gravity bouncing all over the place. Line is down. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1038 | 2008-09-02 01:24 | Found replacement. Unit has been configured and installed
216-LS1 | FOR | Incoming line pressure for both the 3" & 6" lines at FOR are not reading correctly. While the 6" is running today, the line psi shows -4 psi and the meter psi reads 24 psi. Call or email if any Q's. Thx klj | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1136 | 2008-12-17 21:33 | opened both (3" & 6" psi) loops from OMNI output and tied loops into plc input. now scada can see an accurate pressure for both the 3" and 6" incoming pressure transmitters. also changed plc program to reflect the proper alarm setpoints which now match our DOT records.
216-LS1 | FOR | Meter 97 Prover not working | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1626 | 2009-05-08 16:44 | The prover at Fort Worth Delivery has no remote or automatic functionality. The current design requires manual/local operation of the prover.
216-LS1 | FOR | OMNI HMI Fail @ Fort Worth (3" & 6") | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1629 | 2009-05-24 19:25 | Brian Gasperino looked into this malfunction and there was no alarm condition. It hasn't come back. Possibly caused by a power failure.
216-LS1 | FOR | Fort Worth 6" VLV 01 would not close. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-1630 | 2009-05-30 19:22 | Found short in conduit between the 480VAC breaker panel and the 6" MOV. Bought wire & repulled to the 6" MOV & the 3" MOV.
216-LS1 | FOR | valve on 6" will not operate @ Fort Worth | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-2333 | 2009-12-05 13:40 | greased and worked valve manually tested ok
216-LS1 | FOR | FW 6", Gravetometer lags behind. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-2452 | 2010-01-22 21:53 | cleaned gravitometer and this corrected the issue
216-LS1 | FOR | Sump is not giving accurate level reading at Ft Worth Delivery. Jumping from 3 ft to 17ft. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-2808 | 2010-05-03 13:56 | cycled power to transmitter, alarms cleared
216-LS1 | FOR | gravitometer at fw (meter 96) is not working..reading 10.0 | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-3476 | 2010-10-22 11:39 | Found a blown fuse, replaced.
216-LS1 | FOR | The gravity that leaves Arlington on the 6" is 62.3 degrees, but the gravitometer at Ft Worth is reading 60.9. One or both of the gravitometers need to be checked. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-3740 | 2011-01-03 04:16 | Checked the gravity at Mtr.94 & Mtr. 97 while flowing. Mtr. 97 gravity was out of tolerance. Adjusted the gravity factor in the Omni to match the flowing API gravity. Will continue to monitor.
216-LS1 | FOR | Com. fail, S/D 6". | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4088 | 2011-03-18 21:52 | fixed by IT
216-LS1 | FOR | The thermal pressure built up on the 6" line, ARL to FT Worth and hit 60 psi while the line was shut down. It gave an alarm and I notified Jeremy. EMT Called Out: Jeramy Welch | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4089 | 2011-02-13 16:17 | thermal pressure was built up while the line was down, this is normal, only 60psi was reached, no harm done
216-LS1 | ARL | com. loss at FW 6". | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4315 | 2011-08-19 03:57 | Communications restored.
216-LS1 | ARL | The gravity at Arlington on the 3" is different than the gravity at Ft Worth on the 3". At Arlington it reads 36.1 and at Ft Worth it is 34.7. | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4430 | 2011-10-13 20:21 | There is no densitometer on the 3" at Arlington Station. Op-Tech's enter the gravity in the profile on the OMNI HMI for the flowing product.
216-LS1 | FOR | For Worth Meter 97 reading 25 bbls an hour higher than Arlington meter. Could not prove. EMT Called Out: Rodney Burton | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4523 | 2011-11-10 17:08 | Cody pulled Meter 97 and the strainer, inspected & cleaned them.
216-LS1 | FOR | Called Rodney out to prove the 3" at Ft worth. We were getting an imbalance. After he proved the meter the problem was corrected. EMT Called Out: Rodney Burton | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4950 | 2012-07-25 22:39 | Proved Mtr. 96. The meter pressure was between 3 and 5 psig.
216-LS1 | FOR | 6" prover not proving.. aborting | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4979 | 2012-08-01 17:05 | There is currently no remote control of the prover at this location.
216-LS1 | FOR | meter overage,,needs proved EMT Called Out: Jeramy Welch | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-4981 | 2012-08-01 00:18 | proved the 3" meter several times until the leak warn system was operating normally
216-LS1 | ARL | Cannot get a good prove on meter #94 | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-5038 | 2012-09-07 00:47 | master link on chain broke jeramy replaced the master link
216-LS1 | FOR | Cannot get a good prove on meter #97 EMT Called Out: Cody Rogers | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-5039 | 2012-09-07 00:46 | pulled meter and strainer, switched to unit 7 and it proved fine
216-LS1 | FOR | HMI fail on 10/2/2012 | 3" ARL to Love Field (OOS in Place) | 7-216-LS1 | AR-5093 | 2012-10-07 22:09 | Had to re-boot the Omni HMI a couple of times to get the alarm to clear.
216-LS3 | ARL | VLV03 would not fully open shows in travel, valve will close ... EMT Called Out: Rodney Burton | 6" ARL to Ft. Worth Delivery | 7-216-LS3 | AR-5357 | 2013-04-17 16:17 | Found tight spot during travel, lubed, worked valve several times and adjusted th open torque switch .
216-LS3 | FOR | HMI FAIL ... EMT Called Out: NONE ... throughput_loss: No | 6" ARL to Ft. Worth Delivery | 7-216-LS3 | AR-5625 | 2013-10-06 19:20 | Nothing showing HMI fail alarm locally. Rebooted the Omni HMI and the alarm cleared
217-LS | ARL | Meter 87 gravitometer not working. ... During delivery from ARL to DAL, the gravity read 53.5 the whole time. The composite on tank was 62. ... Per Lionel Bell. EMT Called Out: Cody Rogers | 8" Arlington to Irving | 7-217-LS | AR-5226 | 2013-01-09 21:22 | flushed gravitometer and calibrated
232-LS | DAL | dallas prover will not prove or trial prove | 12" line Irving Meter Sta to Texaco | 7-232-LS | GV-18453 | 2008-01-20 09:16 | Arlington district took care of this.
233-LS | IRV | Irving meter 14 not reading correct gravity. Reading 44.6 with 38.3 gravity going by station | 12" line Irving Meter Sta to Shell | 7-233-LS | AR-1047 | 2008-11-20 10:36 | Found densitometer pump not running. The pump motor relay wasn't picked up. S-101 open status should pick up the relay. The control voltage fuse was blown in S-101. Replaced the fuse. The pump motor kicked on and the gravity started reading correctly.
234-LS | CTJ | fix air conditioner at carrolton jct | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-3151 | 2010-08-17 20:03 | replaced the air conditioner
234-LS | CTJ | Gravity pump does not seem to be working correctly. With oil crossing station, station was showing 65.0 gravity. Should've been 39.8 gravity. Troubleshoot and repair | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-3580 | 2010-11-23 10:59 | replaced motor and tested ok
234-LS | CTJ | Comm. in and out @ Carrollton Jct. | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-4131 | 2011-05-31 03:58 | worked with Hughes to repair the satellite
234-LS | CTJ_GRP_ROBV049.82 | ROBV 49.8... Maint. Alert | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-4266 | 2011-07-25 15:00 | liquid level high, pumped out water
234-LS | CTJ | Gravitometer not working properly. Bouncing up and down. | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-4621 | 2012-01-23 17:45 | flushed all gravitometers
234-LS | CTJ | Comm. loss, Ct. Jct | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-4624 | 2012-01-20 19:12 | installed new T1 line
234-LS | CTJ | Comm loss at Carrolton Junction. Line went to low mode | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-4849 | 2010-10-11 22:11 | installed new t1 line at all stations, this resolved all comm issues
234-LS | RCH_CTJ_ROBV039.49 | ROBV 39.5 VAULT LIQUID LEVEL HI-HI..... EMT Called Out: Cody Rogers | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-4992 | 2012-08-18 04:43 | worked on pump float was stuck
234-LS | CTJ | Gravity no flow ... EMT Called Out: NONE | 12" line Carrollton Jct. to Irving | 7-234-LS | AR-5445 | 2013-06-19 10:25 | replaced coupling on the gravitometer with jeramy
235-LS | CTJ | Valve B-117 failed to open on switch to Ftw. EMT Called Out: Cody Rogers | 12" line Grapevine Station to Fina | 7-235-LS | AR-4086 | 2011-03-20 20:57 | 238MF07 - 12" Line Grapevine to Chevron Station Including Chevron Station: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check Sheets 1633 Malfunction [ ] Pass [ ] Fail Comment:___________________________________ 238MF07 - 12" GRAPEVINE TO CHEVRON STATION (including Chevron Station): 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check Sheets 1633 Malfunction [ ] Pass [ ] Fail Comment. Valve was pressured up so bled off pressure and operated fine
235-LS | CTJ | Valve B-117 failed to open on switch from Grp. to Ft. Worth. EMT Called Out: Cody Rogers | 12" line Grapevine Station to Fina | 7-235-LS | AR-4087 | 2011-03-20 20:25 | Valve was pressured up bled off pressure and checked operation and worked fine
237-JT | CTJ | comm. loss | Carrolton Junction | 7-237-JT | GV-24355 | 2013-04-15 17:24 | Malfunction sent to wrong area. Reported malfunction to Jeramy Welch for repair.
237-LS | CTJ | Graphic Panel, HMI | Richardson to GRP incl Carrollton | 7-237-LS | GV-10126 | 2005-02-25 13:45 | No graphic Panel Only MCC
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-10128 | 2005-02-25 13:45 | This is to be disconnected/removed. Not used
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-11302 | 2005-08-25 14:51 | System is no longer connected to mainline. Unable to run.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-11466 | 2005-09-25 12:25 | Still cannot run no connction to mainline.
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | GV-12834 | 2006-04-25 13:05 | 231P02M - Area Lighting: No task sheet for this task. Check Sheets 4 Replace burned out bulbs. [ ] Pass [ ] Fail Comment:___________________________________ 5 Check photocell operations. [ ] Pass [ ] Fail Comment:___________________________________ 6 Clean lenses and inspect gaskets and guards when replacing bulbs. [ ] Pass [ ] Fail Comment:___________________________________
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-13546 | 2006-07-25 12:50 | Can't run. PD Pump.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-15179 | 2007-03-25 18:37 | PD Pump disconnected & can't run.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-15350 | 2007-04-25 14:50 | Can't run PD pump - Disconnected.
237-LS | CTJ | Sump, Oil Water Separator System | Richardson to GRP incl Carrollton | 7-237-LS | GV-15352 | 2007-04-25 14:50 | Pump disconnected, no low level stop. High level is set at 24" and is local and supervisory indication only- Does not isolate the station.
237-LS | CTJ | Control Instruments | Richardson to GRP incl Carrollton | 7-237-LS | GV-15642 | 2007-05-25 13:26 | Digital recorder at this location.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-15646 | 2007-05-25 13:26 | PD Pump disconnected - can't run.
237-LS | CTJ | Air Conditioning System | Richardson to GRP incl Carrollton | 7-237-LS | GV-15809 | 2007-06-25 13:49 | N/A
237-LS | CTJ | Control Instruments | Richardson to GRP incl Carrollton | 7-237-LS | GV-15811 | 2007-06-25 13:49 | Paperless recorder at this location.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-15816 | 2007-06-25 13:49 | Pump Disconnected & not in use.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-15817 | 2007-06-25 13:49 | Pump disconnected & not in use.
237-LS | CTJ | Control Instruments | Richardson to GRP incl Carrollton | 7-237-LS | GV-16063 | 2007-07-25 12:20 | Parerless recorder at this location
237-LS | CTJ | Graphic Panel, HMI | Richardson to GRP incl Carrollton | 7-237-LS | GV-16069 | 2007-07-25 12:20 | No filters, used compressed air to dust
237-LS | CTJ | Gravitometers | Richardson to GRP incl Carrollton | 7-237-LS | GV-16072 | 2007-07-25 12:20 | N/A
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-16073 | 2007-07-25 12:20 | PD pump disconnected, can't run.
237-LS | CTJ | Sump, Oil Water Separator System | Richardson to GRP incl Carrollton | 7-237-LS | GV-16075 | 2007-07-25 12:20 | The High-High is local & supervisory indication only.
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | GV-16346 | 2007-08-25 16:48 | North light is out. Broke the pole over, replaced the bulb and cleaned the lens & gasket. Taped the photo cell again and the light still didn't come on. Checked to make sure there was 480VAC all the way to the light and there was. Will try another bulb and take a new transformer with me to make sure the replacement bulb wasn't bad and replace the transformer if necessary.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-16351 | 2007-08-25 16:48 | PD pump disconnected, can't run.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-16537 | 2007-09-25 14:56 | PD pump disconnected - can't run
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | GV-16703 | 2007-10-25 13:13 | The North light on the West pole is out.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-16713 | 2007-10-25 13:13 | PD pump disconnected - can not run.
237-LS | CTJ | Sump, Oil Water Separator System | Richardson to GRP incl Carrollton | 7-237-LS | GV-16715 | 2007-10-25 13:14 | Sump transmitter & Eurotherm give an alarm that provides Supervisory and Local Alarms only. No S/D & isolation.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-16995 | 2007-11-25 19:22 | PD pump disconnected, can't run.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | GV-17160 | 2007-12-25 13:46 | Pump Disconnected.
237-LS | CTJ | Station Valves 4" or Larger | Richardson to GRP incl Carrollton | 7-237-LS | GV-17163 | 2007-12-25 13:46 | Lubed the Valves when doing the semi-annual DOT Inspections.
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | AR-3 | 2008-01-25 16:49 | The light is bad again that just had a new ballast & cap installed. Will repair later.
237-LS | CTJ | Gravitometers | Richardson to GRP incl Carrollton | 7-237-LS | AR-12 | 2008-01-25 16:49 | N/A
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-13 | 2008-01-25 16:49 | PD Pump disconnected - Can't run.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-118 | 2008-02-25 13:34 | PD pump disconnected - can't run.
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | AR-177 | 2008-03-26 02:28 | 3 lights out. Will repair soon.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-182 | 2008-03-26 02:28 | Can't run PD pump - disconnected.
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | AR-242 | 2008-04-25 12:47 | Replaced the ballast, cap. & bulb in the north light on the west pole.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-252 | 2008-04-25 12:47 | Can't run PD pump - disconnected.
237-LS | CTJ | Sump, Oil Water Separator System | Richardson to GRP incl Carrollton | 7-237-LS | AR-254 | 2008-04-25 12:47 | N/A
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-393 | 2008-05-25 18:40 | Can't run pump - Disconnected.
237-LS | CTJ | Air Conditioning System | Richardson to GRP incl Carrollton | 7-237-LS | AR-457 | 2008-06-25 14:49 | N/A
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | AR-458 | 2008-06-25 14:49 | Replaced the ballast & cap. in the South light on the West pole.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-464 | 2008-06-25 14:50 | N/A Pump Disconnected.
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-465 | 2008-06-25 14:50 | PD Pump disconnected - can't run.
237-LS | CTJ | Station Valves 4" or Larger | Richardson to GRP incl Carrollton | 7-237-LS | AR-469 | 2008-06-25 14:50 | Did not lube the valve stems, they are already well lubed.
237-LS | CTJ | Area Lighting | Richardson to GRP incl Carrollton | 7-237-LS | AR-580 | 2008-07-25 12:15 | Replaced the ballast & cap. in the south light on the west pole.
237-LS | CTJ | Gravitometers | Richardson to GRP incl Carrollton | 7-237-LS | AR-590 | 2008-07-25 12:15 | N/A
237-LS | CTJ | Injection, Transfer Pump | Richardson to GRP incl Carrollton | 7-237-LS | AR-591 | 2008-07-25 12:15 | PD pump disconnected - can't run.
237-LS | CTJ | Carrolton junction lossed power. | Richardson to GRP incl Carrollton | 7-237-LS | AR-690 | 2008-06-18 11:05 | There was a widespread power outage that affected Carrollton Jct. Jeramy Welch monitored until power was restored.
237-LS | CTJ | Valve at Carrollton Jct.to Grapevine may be leaking during delivery to Dallas. Pressure at Grapevine climbed while pumping to Dallas and the leak profile showed packing the line to Grapevine. | Richardson to GRP incl Carrollton | 7-237-LS | AR-1316 | 2009-01-20 23:19 | adjusted limits on valve to ensure a better seal
237-LS | RCH_CTJ_ROBV039.49 | power outage MP 39.5 tech has been to block valve to do on site check Account #: 237.12 | Richardson to GRP incl Carrollton | 7-237-LS | AR-1771 | 2009-06-12 20:11 | power outage due to storms, checked block valve everything ok
237-LS | RCH_CTJ_ROBV039.49 | MP 39.5 on the 12". "Maint. Alert". Called EMT and will check on it in the a.m. | Richardson to GRP incl Carrollton | 7-237-LS | AR-2245 | 2009-11-15 23:58 | 231MF07 - 12" Line Greenville to Carrolton Junction Including Carrolton Junction: Check Sheets 1633 Malfunction [ ] Pass [ ] Fail Comment:___________________________________ Repaired float switch on vault water pump tested ok
237-LS | CTJ | flasher alarm still in window | Richardson to GRP incl Carrollton | 7-237-LS | AR-2814 | 2010-01-12 01:50 | changed flasher sensors back to the "A" side to remove the alarm from the HMI
237-LS | CTJ | Comm loss @ CTJ. IRV, and DAL on the 12". Keeps knocking 2nd unit down at GRV. | Richardson to GRP incl Carrollton | 7-237-LS | AR-3064 | 2010-05-09 07:13 | comm fails cleared
237-LS | CTJ | Numerous Comm losses at station. | Richardson to GRP incl Carrollton | 7-237-LS | AR-3139 | 2010-08-11 13:09 | repaired by IT department
237-LS | CTJ | On switching from FW to DAL, S102 going to IRV at CTJ would not open, shut the 12" down. Tried to close B103 going to GRP after line was down, it would not close. On my screen, I had status of comm. and no power loss. EMT Called Out: Rodney Burton | Richardson to GRP incl Carrollton | 7-237-LS | AR-3478 | 2010-11-20 21:09 | The wires, from the push buttons for the valve controls, were laying in the bottom of each of the valves bucket in the MCC and appeared to be functional , but were not connected to the terminal strips. Landed the wires from the push buttons to the remote common, remote open & remote close on the terminal strips.
237-LS | RCH_CTJ_ROBV039.49 | ROBV 39.5 Vault Liquid Level Hi-Hi alarm. EMT Called Out: Jeramy Welch | Richardson to GRP incl Carrollton | 7-237-LS | AR-3599 | 2010-09-07 16:29 | repaired vault water pump
237-LS | CTJ | COMM LOSS and made GVL shutdown. | Richardson to GRP incl Carrollton | 7-237-LS | AR-4103 | 2010-09-17 08:07 | installed new t1 lines at all the stations, this resolved our comm issues
237-LS | CTJ | Comm loss at Richardsona and Carrollton. Was running 3 unit rate. comm knocked off units at GRV and RCH. No storms in area. | Richardson to GRP incl Carrollton | 7-237-LS | AR-4104 | 2010-10-13 08:09 | installed new t1 lines at all stations, this resolved our comm issues
237-LS | CTJ | Lost comm again knocking off pumps at RCH and GVL again | Richardson to GRP incl Carrollton | 7-237-LS | AR-4105 | 2010-10-18 10:51 | installed new t1 lines to all stations, this relolved the comm issues
237-LS | RCH_CTJ_ROBV039.49 | Security alarm coming in and out at 39.5 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4129 | 2011-05-24 18:16 | adjusted mounting bracket on lid enclosure
237-LS | RCH | Richardson pump will not run. Apparent problem with suction valve. Brandon notified. EMT Called Out: Brandon Hoelscher | Richardson to GRP incl Carrollton | 7-237-LS | AR-4268 | 2011-08-10 19:19 | this malfunction was written up incorrectly, Richardson station is in the Greenville area
237-LS | RCH_CTJ_ROBV039.49 | mp 39.5 has a Maint. Alert | Richardson to GRP incl Carrollton | 7-237-LS | AR-4317 | 2011-08-17 20:13 | replaced surge suppressor
237-LS | CTJ | Valve B-103 @ Carrollton Jct. is not holding pressure. | Richardson to GRP incl Carrollton | 7-237-LS | AR-4441 | 2011-10-28 00:03 | adjusted limits on valve to get better seal
237-LS | RCH_CTJ_ROBV039.49 | maint. alert robv 39.5 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4609 | 2011-10-21 13:21 | water was in electrical jct boxes, removed the water and repaired the wire nuts. 231MF07 - 12" GREENVILLE TO CARROLTON JUNCTION (includes Carrolton Junction): 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check Sheets 1633 Malfunction [ ] Pass [ ] Fail Comment:___________________________________ found water level high ...pumped water out
237-LS | CTJ_GRP_ROBV049.82 | ROBV 49.8 Seal Fail alarm and Vault Liquid Level HI-HI alarms received. Brandon notified. | Richardson to GRP incl Carrollton | 7-237-LS | AR-4618 | 2012-01-25 14:28 | pumped water out of vault
237-LS | RCH_CTJ_ROBV030.47 | ROBV @ 30.5 communications in & out numerous times over the last several hours. | Richardson to GRP incl Carrollton | 7-237-LS | AR-4620 | 2012-01-25 12:53 | thunder storms in the area caused these comm failures
237-LS | RCH_CTJ_ROBV039.49 | ac voltage fail mp 39.5 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4681 | 2012-02-25 14:14 | Found a fault on the AC surge suppressor module. It will be replaced when a new one comes in.
237-LS | RCH_CTJ_ROBV039.49 | also maint. alert 39.5 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4683 | 2012-02-25 14:19 | The maintenance alert is because the AC Surge Suppressor Module has gone bad. A new one is being ordered to replace it.
237-LS | RCH_CTJ_ROBV039.49 | Maint. Alert MP 39.5.... recieved 1/19/2012 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4789 | 2012-03-26 13:14 | replaced ac surge supressor and tested ok
237-LS | RCH_CTJ_ROBV039.49 | ac votae Fail ..Valve control mp 39.5....03/20/2012 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4790 | 2012-03-26 13:12 | replaced ac surge supressor and tested ok
237-LS | CTJ_GRP_ROBV049.82 | Seal Fail mp 49.8 3/20/2012 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4791 | 2012-03-26 13:09 | we do not have a pump in this vault, seal fail was caused due to excessive water in the vault, i pumped the water out of the vault and cleared the alarm
237-LS | RCH_CTJ_ROBV039.49 | Comm. fail at ROBV 39.5 | Richardson to GRP incl Carrollton | 7-237-LS | AR-4894 | 2012-06-01 22:00 | power outage caused this comm fail, power restored...comms came back
237-LS | CTJ | Valve B103 bleeding pressure by towards Grapevine | Richardson to GRP incl Carrollton | 7-237-LS | AR-4937 | 2012-07-03 12:22 | cycled valve closed manualy then cycled again and seemed to be closing all the way and sealing
237-LS | RCH_CTJ_ROBV039.49 | ROBV 39.5 Vault liquid level high high Cody called will respond in AM | Richardson to GRP incl Carrollton | 7-237-LS | AR-4985 | 2012-08-15 08:00 | GFCI was tripped causing the sump pump to not run. I wired the pump directly into the breaker to eliminate unwanted tripping.
237-LS | RCH_CTJ_ROBV030.47 | ROBV 30.5 Maintenance Alert EMT Called Out: Jeramy Welch | Richardson to GRP incl Carrollton | 7-237-LS | AR-4986 | 2012-08-15 11:53 | sump pump was not running properly, i had to adjust the float brackets on the pump to allow the pump to run
237-LS | RCH_CTJ_ROBV039.49 | M.P 39.5 R.O.B.V Maintenance Alert Alarm Active EMT Called Out: Cody Rogers | Richardson to GRP incl Carrollton | 7-237-LS | AR-4990 | 2012-08-19 14:24 | adjusted pump
237-LS | RCH_CTJ_ROBV039.49 | Maintenance Alert at M.P. 39.5 R.O.B.V | Richardson to GRP incl Carrollton | 7-237-LS | AR-4991 | 2012-08-18 11:35 | worked on pump float was hung up
237-LS | RCH_CTJ_ROBV030.47 | ROBV 30.5 alarm. ... Valve Control ... AC Voltage Fail EMT Called Out: Cody Rogers | Richardson to GRP incl Carrollton | 7-237-LS | AR-5036 | 2012-09-10 21:18 | found flakey relay
237-LS | CTJ | B-103 at Carrolton Junction bleeding by to Grapevine when delivering to Dallas. | Richardson to GRP incl Carrollton | 7-237-LS | AR-5043 | 2012-08-16 15:26 | adjusted limits on actuator to make a better seal
237-LS | RCH_CTJ_ROBV039.49 | Security Alarm at M.P 39.5 R.O.B.V | Richardson to GRP incl Carrollton | 7-237-LS | AR-5095 | 2012-08-17 11:20 | adjusted the lid prox switch and tested ok
237-LS | RCH_CTJ_ROBV039.49 | Downstream PSI transmitter not reading correctly. Shows -375. EMT Called Out: Jeramy Welch | Richardson to GRP incl Carrollton | 7-237-LS | AR-5096 | 2012-10-08 15:21 | transmitter was not powered up when i arrived, i replaced some wire nuts and reset the 24 volt dc breaker and verifted the transmitter was operating correctly.
237-LS | RCH_CTJ_ROBV039.49 | CCT went from a 1 unit rate to 3 unit rate and recieved an MOP Exceedence Alarm, The Pressure transmiter on the downstream side of 39.5 ROBV was showing incorrect pressure EMT Called Out: Rodney Burton | Richardson to GRP incl Carrollton | 7-237-LS | AR-5097 | 2012-10-10 07:32 | found that the MI cable on the pressure transmitter was causing the loop current to read high, we replaced the MI cable and problem was solved
237-LS | CTJ | Block Valve B103 @ Carrrollton Jct. will not go closed. Shows to be in travel. | Richardson to GRP incl Carrollton | 7-237-LS | AR-5099 | 2012-10-25 08:49 | adjusted close limit on actuator and added grease to stem
237-LS | CTJ | Gravitometer not working. From jet to gas, stopped at 44.0 gravity. EMT Called Out: Rodney Burton | Richardson to GRP incl Carrollton | 7-237-LS | AR-5137 | 2012-11-03 12:00 | Flushed the densitometer and verified the gravity with the CCT and a hydrometer.
237-LS | RCH_CTJ_ROBV030.47 | AC VOLTAGE FAIL MP 30.5 EMT Called Out: Rodney Burton | Richardson to GRP incl Carrollton | 7-237-LS | AR-5145 | 2012-11-23 16:27 | Power was restored when I arrived. Checked out power components anyway and all was good.
237-LS | RCH_CTJ_ROBV030.47 | ROBV 30.5 AC Voltage fail, Maint Alert and Valve Control alarms EMT Called Out: Rodney Burton | Richardson to GRP incl Carrollton | 7-237-LS | AR-5146 | 2012-11-23 16:31 | Power was restored when I arrived. Checked out power components anyway and all was good.
237-LS | CTJ | comm loss ...going in and out | Richardson to GRP incl Carrollton | 7-237-LS | AR-5259 | 2013-02-14 11:26 | ck station and verified all comm issues were resolved via the IT department
237-LS | CTJ | Gravitometer not reading correctly @ Carrollton Jct. Oil gty of 39.1 reading 51.5 | Richardson to GRP incl Carrollton | 7-237-LS | AR-5296 | 2013-02-05 22:09 | found bad motor, replaced and tested ok
237-LS | CTJ | Gravitometer at Carrolton Jct not tracking. ... EMT Called Out: Rodney Burton | Richardson to GRP incl Carrollton | 7-237-LS | AR-5412 | 2013-05-31 01:42 | Flushed the densitometer and cleaned the strainer.
238-LS | FWT | Protective Devices, Pressure switches, Time delays | 12" GRP to Chevron/Ft. Worth | 7-238-LS | GV-11084 | 2005-07-25 13:56 | 238P12M - Protective Devices, Pressure switches, Time delays: No task sheet for this task. Check Sheets 72 Check pressure switches for leaks. [ ] Pass [ ] Fail Comment:___________________________________
238-LS | FWT | Protective Devices, Pressure switches, Time delays | 12" GRP to Chevron/Ft. Worth | 7-238-LS | GV-13977 | 2006-09-25 15:47 | 238P12M - Protective Devices, Pressure switches, Time delays: No task sheet for this task. Check Sheets 72 Check pressure switches for leaks. [ ] Pass [ ] Fail Comment:___________________________________
238-LS | FWT | Control Instruments | 12" GRP to Chevron/Ft. Worth | 7-238-LS | GV-14140 | 2006-10-25 18:16 | 238P05M - Control Instruments: No task sheet for this task. Check Sheets 19 Check for proper operation of controllers. [ ] Pass [ ] Fail Comment:___________________________________ 20 Inspect pressure transmitters for leaks. [ ] Pass [ ] Fail Comment:___________________________________ 22 Change chart and ink check time on chart recorders where appl. [ ] Pass [ ] Fail Comment:___________________________________ 24 Check temperature transmitters for proper calibration. [ ] Pass [ ] Fail Comment:___________________________________
238-LS | FWT | Sump, Oil Water Separator System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | GV-14150 | 2006-10-25 18:17 | 238P19M - Sump, Oil Water Separator System: No task sheet for this task. Check Sheets 191 Pump. Run manually and check for excessive noise or vibration. [ ] Pass [ ] Fail Comment:___________________________________
238-LS | FWT | Ft. Worth Terminal meter #17 quit working during a delivery. Rodney called-out at 1600. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | GV-16042 | 2007-06-09 21:17 | When I got to the station, I had the CCT open valves to allow flow and checked the signal from the pre-amp with a scope. Everything looked good and we had counts again. A few more deliveries were made with no problems. Verified associated wire termination points were not loose, replaced the pickup coil and pre-amp.
238-LS | FWT | Sump, Oil Water Separator System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-708 | 2008-08-25 19:59 | Sump Empty.
238-LS | FWT | Product Measurment System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-971 | 2008-11-25 14:02 | No prover at this location - check meter only.
238-LS | FWT | Sump, Oil Water Separator System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-975 | 2008-11-25 14:03 | Sump Empty.
238-LS | FWT | Sump, Oil Water Separator System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-1265 | 2009-02-25 15:34 | No product in sump
238-LS | FWT | Product Measurment System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-1341 | 2009-03-25 12:46 | Changed the time in the Elliott for DST.
238-LS | FWT | Sump, Oil Water Separator System | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-1567 | 2009-05-25 13:12 | Sump Empty.
238-LS | FWT | Chevron Fw. Terminal counter quit counting. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-1631 | 2009-05-30 18:40 | Simulated counts & checked all connections from the pick-up coil to the Elliott. Installed a UPS, from commercial power, to power the Elliott. The power in our cabinet was fluctuating and possibly affecting the Elliott.
238-LS | FWT | Meter 17 is not counting causing leak detection alarms in that sector. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-1634 | 2009-05-07 05:47 | Simulated counts & checked all connections from the pick-up coil to the Elliott. Installed a UPS, from commercial power, to power the Elliott. The power in our cabinet was fluctuating and possibly affecting the Elliott.
238-LS | FWT | Station Valves 4" or Larger | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-1974 | 2009-09-25 17:46 | checked all valve, everything ok
238-LS | FWT | com. loss@ Ftw./Chv. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-3739 | 2010-10-04 20:41 | Worked with Greg W. to correct. Put comm's back on land line.
238-LS | FWT | Meter factor needs adjusted. Flow rate at FWM is 2693 BPH and 2842 at FWT. Giving me an alarm. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-3747 | 2011-01-26 16:08 | Adjusted the factor in the Elliott to match the Fort Worth Meter Station net flow rate.
238-LS | FWT | Station Monthly Walkthru Pm's | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-4283 | 2011-09-25 12:59 | 238PM00 - Station Monthly Walkthru Pm's: 1. What job or task are you planning to perform? 2. What tools/resources/people will you need to complete the job? 3. What can go wrong that might result in an injury or less than desired outcome? 4. How are you going to mitigate, manage, and /or minimize the probability of an undesirable outcome? Check the following items Control Instruments 1. Check for proper operation of controllers. 2. Inspect pressure transmitters and Switches for leaks 3. Check time on chart recorders. Graphic panel, SCC, Instrument panel, Metering panel and Switchgear fronts. 1. Replace burned out light bulbs Product Measurement System 1. Verify volume in flow computer monthly and when powered down. 2. Check the computer printer for proper operation. 3. Check parameters in metering cabinet flow computer. Thermal relief valves. 1. Check thermal relief valves for leaks. Daniel Control Valve 1. Check for leaks 2. Blow down filters. Sump Pump 1. Check motor and pump for excessive noise and vibration. 2. Check for leaks.
238-LS | FWT | Ft. Worth terminal comm. loss. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-4602 | 2011-11-25 15:53 | Corrected by Tulsa - EMT not notified of Comm's problem.
238-LS | FWT | Lots of Comm. fails all night. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-4615 | 2011-11-25 09:19 | Corrected without EMT involvement.
238-LS | FWT | Station Quarterly Walkthru PM's | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-4760 | 2012-04-25 16:37 | Due to new PM structure this station's quarterly has been eliminated. 238PQ00 - Station Quarterly Walkthru PM's:
238-LS | FWT | Station Quarterly Walkthru PM's | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-5063 | 2012-10-25 19:13 | N/A
238-LS | FWT | TRAP VALVES[INLET&outlet] WOULD NOT OPEN. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-5132 | 2012-09-29 21:50 | Wires were found crossed from recent switch, push buttons and contact block replacements.
238-LS | FWT | Trap valves will not open. | 12" GRP to Chevron/Ft. Worth | 7-238-LS | AR-5133 | 2012-10-02 12:34 | Wires were found crossed from recent switch, push buttons and contact block replacements.
239-LS | GRP | Flasher Fail | 12" Grapevine to Nustar | 7-239-LS | AR-4440 | 2011-10-23 16:40 | cleared alarm, it was due to fill timeout, tested and worked properly
243-LS | GRP | 8" pumps intermitently go down. No alarms ... EMT Called Out: Jeramy Welch | 8" GRP to DFW (INC Airport Meter) | 7-243-LS | AR-5444 | 2013-06-17 22:26 | Occasional, momentary drop of valve open status signal from Allied Aviation seems to be causing an issue with uncommanded S/D's. Working with Engineering to get a short timer in the logic to prevent the S/D of the unit immediately upon signal loss. Will update when complete. -RKB (This malfunction replaced by: AR-5521)
302-LS | HOL_OKM_ROBV493.10 | comm. loss at robv493.1 | All remaining 8" Oklahoma Assets | 7-302-LS | GP-20094 | 2010-02-01 01:44 | Valve lost power due to storms in area.
314-LS | BEL | Flush All Identified Dead Legs | Total to Bell Jct | 7-314-LS | AR-4474 | 2011-11-25 13:59 | station in nitrogen